## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-07-2025 | during | 01-08-2025 | during | 01-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 146 | 141 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 197 | 198 | 208.13 | 208.13 | 197 | 197 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 332 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 16.2 | 45.5 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 31 | 149.36 | 149.36 | 144 | 144 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 30 | 17 | 55 | 55 | 55 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 28 | 23 | 33 | 33 | 28 | 28 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 6 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 25 | 52.19 | 52.19 | 25 | 25 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 32 | 86 | 149 | 149 | 114 | 114 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 87 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 50 | 94 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 6 | 0 | 17 | 0 | 17 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 550 | 500 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 733.79 | 733.79 | 380 | 380 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 90 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 2050.2 | 2264.5 | 5235.94 | 5218.94 | 4165.47 | 4148.47
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 4 | 0 | 8 | 0 | 8 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 23 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 219 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 220 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 32 | 80 | 80 | 98 | 98 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 31 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0.41 | 0 | 1.44 | 0 | 1.44 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 7 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1045 | 1145 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 17.59 | 20 | 15 | 20 | 15 | 20 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 757 | 758 | 770 | 770 | 770 | 770 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2279 | 2537 | 3754.16 | 3772.72 | 3596.16 | 3614.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 203 | 196 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 346 | 353 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 154 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 35 | 32 | 46.7 | 46.7 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 43 | 48 | 55 | 55 | 48 | 48 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 16 | 195 | 195 | 185 | 185 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 30 | 120 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 42 | 43 | 47 | 47 | 47 | 47 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 15 | 120 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 30 | 30 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 52 | 53 | 113 | 113 | 46 | 46 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 39 | 0 | 45 | 0 | 45 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1367 | 1647 | 2424.56 | 2379.56 | 2205.36 | 2160.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-07-2025 | during | 01-08-2025 | during | 01-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 80 | 81 | 157.5 | 157.5 | 102 | 102 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 150 | 200 | 200 | 170.2 | 170.2 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 104 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 15.69 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 275.69 | 364 | 595.9 | 549 | 466.1 | 419.2
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 70 | 70 | 70 | 70 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 133 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 0 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 74 | 83 | 83 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 7 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 110 | 341 | 341 | 0 | 0 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 371 | 374 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 300 | 290 | 290 | 290 | 290 | 290 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1023 | 1066 | 1405 | 1405 | 1018 | 1018
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 428 | 432 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 2 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 206 | 205 | 410 | 410 | 246 | 246 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 49.75 | 0 | 25 | 0 | 25 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 956 | 1216 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1677.75 | 1910 | 3241.2 | 3216.2 | 2935.2 | 2910.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 306 | 304 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 994 | 1110 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 232 | 277 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.34 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1872.34 | 2031 | 2162 | 2161 | 2102 | 2101
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 1.48 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 205 | 203 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 196 | 198 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 198 | 198 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 410 | 353 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 27 | 27 | 27 | 27 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 87 | 87 | 87 | 87 | Engine Problem
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.11 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1173 | 1315.96 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 25.17 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 16 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 2227.76 | 2317.96 | 3174.47 | 3009.87 | 3133.09 | 2968.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 156 | 160 | 150 | 150 | 150 | 150 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.4 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 159 | 0 | 152.25 | 0 | 152.25 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 455.4 | 387 | 600.85 | 412 | 600.85 | 412
System Total |  |  |  |  | 28671.2 | 27843.665 | 13228.14 | 14524.46 | 22594.08 | 22124.29 | 20222.23 | 19752.44
Forecast Scenario (01-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14320 |  | 0 |  | 14320
|  |  |  | 1:00 | 13970 |  | 0 |  | 13970
|  |  |  | 2:00 | 13680 |  | 0 |  | 13580
|  |  |  | 3:00 | 13320 |  | 0 |  | 13220
|  |  |  | 4:00 | 12990 |  | 0 |  | 12890
|  |  |  | 5:00 | 12900 |  | 0 |  | 12800
|  |  |  | 6:00 | 12080 |  | 0 |  | 11980
|  |  |  | 7:00 | 11780 |  | 0 |  | 11680
|  |  |  | 8:00 | 11630 |  | 0 |  | 11530
|  |  |  | 9:00 | 11440 |  | 0 |  | 11340
|  |  |  | 10:00 | 11470 |  | 0 |  | 11370
|  |  |  | 11:00 | 11690 |  | 0 |  | 11590
|  |  |  | 12:00 | 12150 |  | 0 |  | 12050
|  |  |  | 13:00 | 12880 |  | 0 |  | 12780
|  |  |  | 14:00 | 12300 |  | 0 |  | 12200
|  |  |  | 15:00 | 12370 |  | 0 |  | 12270
|  |  |  | 16:00 | 12080 |  | 0 |  | 11980
|  |  |  | 17:00 | 11560 |  | 0 |  | 11460
|  |  |  | 18:00 | 10990 |  | 0 |  | 10890
|  |  |  | 18:30 | 11500 |  | 0 |  | 11400
|  |  |  | 19:00 | 12410 |  | 0 |  | 12310
|  |  |  | 19:30 | 13580 |  | 0 |  | 13480
|  |  |  | 20:00 | 13670 |  | 0 |  | 13570
|  |  |  | 21:00 | 14240 |  | 0 |  | 14140
|  |  |  | 22:00 | 14300 |  | 0 |  | 14200
|  |  |  | 23:00 | 14500 |  | 0 |  | 14400
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 12050.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14140.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14240.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 304.72 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:50 hrs on 01-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 31-07-2025 | [28 empty] | Date: | 31-07-2025 | [28 empty] | Date: | 31-07-2025 | [28 empty] | Date: | 31-07-2025 | [28 empty] | Date: | 31-07-2025 | [12 empty] | Date: | 31-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [12 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.6 | 35 | 97 | 30 | 293 | 15 | 35 | 90 | 0 | 450 | 149 | 500 | 0 | 17 | 335 | 198 | 0 | 0 | 142 | 26 | 22 | 0 | 0 | 0 | 0 | 56 | 0 | 16 | 65 | 68 | 0 | 12 | 12 | 0 | 219 | 0 | 32 | 686 | 0 | 0 | 19 | 8 | 0 | 220 | 0 | 0 | 0 | 1130 | 0 | 51 | 30 | 185 | 0 | 355 | 0 | 48 | 191 | 35 | 99 | 30 | 161 | 63 | 20 | 71 | 46 | 43 | 0 | 44 | 0 | 300 | 360 | 0 | 60 | 146 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 104 | 150 | 80 | 0 | 0 | 12 | 7936.6 | 428 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 0 | 1439 | 0 | 0 | 0 | 0 | 35 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 197 | 0 | 198 | 0 | 397 | 0 | 0 | 156 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 120 | 220 | 0 | 305 | 1232 | 0 | 6824 | 14760.6 | 105.68
01:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 35 | 96 | 15 | 15 | 0 | 17 | 54 | 0 | 450 | 152 | 500 | 0 | 17 | 335 | 198 | 0 | 0 | 125 | 26 | 22 | 0 | 0 | 0 | 0 | 48 | 0 | 11 | 65 | 39 | 0 | 12 | 12 | 0 | 220 | 0 | 32 | 700 | 0 | 0 | 19 | 8 | 0 | 221 | 0 | 0 | 0 | 1142 | 0 | 51 | 30 | 185 | 0 | 354 | 0 | 49 | 195 | 35 | 98 | 30 | 162 | 58 | 20 | 75 | 44 | 43 | 0 | 44 | 0 | 295 | 379 | 0 | 60 | 145 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 5 | 104 | 130 | 101 | 0 | 0 | 11 | 7515 | 429 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1132 | 0 | 1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 197 | 0 | 198 | 0 | 405 | 0 | 0 | 164 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 304 | 1232 | 0 | 6800 | 14315 | 105.69
02:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 153 | 500 | 0 | 0 | 335 | 198 | 0 | 0 | 108 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 50 | 0 | 0 | 12 | 12 | 0 | 220 | 0 | 33 | 729 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1144 | 0 | 51 | 0 | 185 | 0 | 351 | 0 | 49 | 200 | 35 | 99 | 30 | 161 | 58 | 20 | 81 | 44 | 43 | 0 | 44 | 0 | 295 | 388 | 0 | 60 | 134 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 104 | 130 | 101 | 0 | 0 | 9 | 7228 | 428 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1081 | 0 | 1419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 197 | 0 | 198 | 0 | 414 | 0 | 0 | 165 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 120 | 220 | 0 | 305 | 1232 | 0 | 6691 | 13919 | 105.7
03:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 150 | 500 | 0 | 0 | 335 | 135 | 0 | 0 | 90 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 29 | 0 | 0 | 12 | 12 | 0 | 219 | 0 | 25 | 700 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1043 | 0 | 51 | 0 | 185 | 0 | 354 | 0 | 49 | 193 | 35 | 103 | 30 | 162 | 63 | 20 | 64 | 42 | 8 | 0 | 43 | 0 | 295 | 386 | 0 | 60 | 139 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 95 | 110 | 101 | 0 | 0 | 12 | 6904 | 428 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1054 | 0 | 1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 197 | 0 | 197 | 0 | 414 | 0 | 0 | 164 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 120 | 220 | 0 | 305 | 1232 | 0 | 6558 | 13462 | 105.71
04:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 152 | 500 | 0 | 0 | 335 | 135 | 0 | 0 | 70 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 12 | 12 | 0 | 219 | 0 | 33 | 694 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1045 | 0 | 51 | 0 | 185 | 0 | 354 | 11 | 49 | 193 | 35 | 65 | 30 | 155 | 63 | 20 | 60 | 42 | 8 | 0 | 44 | 0 | 295 | 365 | 0 | 60 | 139 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 95 | 110 | 101 | 0 | 0 | 12 | 6772 | 428 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 0 | 1273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 197 | 0 | 196 | 0 | 403 | 0 | 0 | 163 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 120 | 220 | 0 | 305 | 1122 | 0 | 6348 | 13120 | 105.72
05:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 151 | 500 | 0 | 0 | 335 | 133 | 0 | 0 | 52 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 12 | 12 | 0 | 218 | 0 | 35 | 693 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 935 | 0 | 51 | 0 | 185 | 0 | 355 | 58 | 49 | 190 | 35 | 62 | 30 | 144 | 57 | 20 | 58 | 40 | 0 | 0 | 44 | 0 | 295 | 365 | 0 | 60 | 131 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 94 | 85 | 101 | 0 | 0 | 12 | 6629 | 428 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 0 | 1274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 197 | 0 | 196 | 0 | 405 | 0 | 0 | 165 | 0 | 70 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 120 | 220 | 0 | 305 | 1121 | 0 | 6276 | 12905 | 105.73
06:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 153 | 500 | 0 | 0 | 335 | 133 | 0 | 1 | 17 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 12 | 12 | 0.07 | 217 | 0 | 35 | 690 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 934 | 0 | 51 | 0 | 185 | 0 | 356 | 22 | 49 | 190 | 35 | 35 | 30 | 100 | 54 | 20 | 44 | 34 | 0 | 0 | 44 | 0 | 295 | 370 | 0 | 60 | 130 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 75 | 65 | 101 | 0 | 1.25 | 12 | 6380.32 | 428 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.15 | 927 | 0 | 1160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0.16 | 207 | 0 | 197 | 0 | 197 | 0 | 343 | 0 | 0 | 165 | 0 | 50 | 1 | 70 | 0 | 0 | 0.3 | 9 | 0.01 | 0 | 228 | 120 | 220 | 0 | 304 | 1020 | 0 | 5908.62 | 12288.94 | 105.74
07:00 | 0 | 40 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 151 | 500 | 0 | 0 | 335 | 133 | 0 | 2 | 17 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0.64 | 217 | 0 | 33 | 697 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 948 | 0 | 51 | 0 | 185 | 0 | 353 | 36 | 48 | 200 | 35 | 31 | 30 | 100 | 56 | 20 | 48 | 34 | 0 | 1 | 44 | 0 | 295 | 385 | 0 | 60 | 138 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 75 | 75 | 101 | 0 | 3.39 | 12 | 6453.03 | 428 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 862 | 0 | 1068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 10 | 0 | 2.95 | 205 | 0 | 197 | 0 | 198 | 0 | 368 | 0 | 0.27 | 165 | 0 | 50 | 3 | 70 | 0 | 0 | 1.1 | 47 | 0.06 | 0 | 231 | 120 | 220 | 0 | 306 | 989 | 0 | 5811.29 | 12264.32 | 105.75
08:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 154 | 500 | 0 | 0 | 335 | 133 | 0 | 2 | 17 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 1.81 | 218 | 0 | 8 | 722 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 954 | 1 | 51 | 0 | 185 | 0 | 350 | 62 | 48 | 200 | 35 | 31 | 40 | 100 | 54 | 20 | 48 | 34 | 0 | 16 | 43 | 0 | 295 | 385 | 0 | 60 | 135 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 75 | 75 | 93 | 0 | 29.13 | 12 | 6569.94 | 428 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 847 | 0 | 1076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 6.68 | 206 | 0 | 200 | 0 | 199 | 0 | 364 | 0 | 0.44 | 162 | 0 | 50 | 11 | 70 | 0 | 0 | 3.3 | 41 | 0.16 | 0 | 231 | 120 | 220 | 0 | 306 | 991 | 0 | 5820.58 | 12390.52 | 105.76
09:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 51 | 0 | 0 | 0 | 13 | 0 | 0 | 400 | 152 | 500 | 0 | 0 | 335 | 135 | 0 | 2 | 17 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 51.4 | 0 | 0 | 0 | 0 | 0 | 0.07 | 219 | 0 | 4 | 738 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 958 | 4 | 51 | 0 | 185 | 0 | 343 | 69 | 48 | 203 | 35 | 16 | 50 | 51 | 51 | 10 | 17 | 34 | 0 | 8 | 44 | 0 | 295 | 388 | 0 | 60 | 141 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 75 | 75 | 92 | 1 | 19.29 | 12 | 6497.76 | 428 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 35 | 864 | 0 | 1079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.23 | 41 | 0 | 4.3 | 205 | 0 | 200 | 0 | 201 | 0 | 383 | 0 | 0.16 | 161 | 0 | 35 | 17 | 34 | 0 | 0 | 3.1 | 54 | 0.19 | 0 | 232 | 120 | 220 | 0 | 305 | 990 | 0 | 5870.98 | 12368.74 | 105.77
10:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 37 | 0 | 0 | 0 | 35 | 0 | 0 | 450 | 152 | 550 | 0 | 0 | 333 | 198 | 0 | 7 | 17 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0.22 | 220 | 0 | 2 | 737 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 958 | 7 | 51 | 0 | 185 | 0 | 338 | 88 | 45 | 207 | 34 | 16 | 70 | 17 | 55 | 10 | 17 | 34 | 0 | 28 | 44 | 0 | 295 | 390 | 0 | 60 | 152 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 75 | 75 | 80 | 0 | 26.32 | 12 | 6658.54 | 428 | 219 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14.96 | 870 | 0 | 1076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.06 | 3 | 0 | 2.8 | 204 | 0 | 200 | 0 | 203 | 0 | 414 | 0 | 0.24 | 162 | 0 | 35 | 17 | 34 | 0 | 0 | 5.1 | 160 | 0.25 | 0 | 232 | 120 | 220 | 0 | 307 | 996 | 0 | 5962.41 | 12620.95 | 105.78
11:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 35 | 32 | 0 | 0 | 0 | 40 | 30 | 0 | 450 | 151 | 550 | 0 | 12 | 335 | 198 | 0 | 22 | 17 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7 | 0 | 0 | 0 | 0 | 0 | 1.72 | 220 | 0 | 4 | 756 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1020 | 4 | 51 | 3 | 185 | 0 | 345 | 103 | 43 | 202 | 34 | 16 | 70 | 17 | 53 | 20 | 17 | 36 | 0 | 22 | 44 | 0 | 295 | 379 | 0 | 60 | 158 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 75 | 75 | 80 | 1 | 46.54 | 12 | 6840.96 | 429 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 59.99 | 908 | 0 | 1106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.84 | 39 | 0 | 18.5 | 205 | 0 | 196 | 0 | 201 | 0 | 414 | 0 | 0.9 | 155 | 0 | 35 | 40 | 34 | 0 | 0 | 7.7 | 106 | 0.39 | 0 | 230 | 120 | 220 | 0 | 304 | 996 | 0 | 6085.32 | 12926.28 | 105.79
12:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2 | 35 | 32 | 0 | 0 | 0 | 55 | 50 | 0 | 450 | 146 | 550 | 0 | 30 | 332 | 197 | 0 | 6 | 17 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17.59 | 0 | 0 | 0 | 0 | 7 | 0.41 | 221 | 0 | 5 | 757 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1045 | 4 | 51 | 30 | 185 | 0 | 346 | 154 | 43 | 203 | 35 | 16 | 70 | 15 | 52 | 20 | 30 | 36 | 0 | 39 | 42 | 0 | 300 | 371 | 0 | 60 | 157 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 75 | 75 | 80 | 1 | 15.69 | 12 | 6994.89 | 428 | 206 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 49.75 | 956 | 0 | 1173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.48 | 16 | 0 | 25.17 | 205 | 0 | 196 | 0 | 198 | 0 | 410 | 0 | 3.11 | 156 | 0 | 70 | 33 | 34 | 0 | 0 | 3.4 | 159 | 0.34 | 0 | 232 | 120 | 220 | 0 | 306 | 994 | 0 | 6233.25 | 13228.14 | 105.8
13:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.7 | 35 | 45 | 16 | 45 | 5 | 55 | 130 | 5 | 450 | 144 | 500 | 0 | 35 | 335 | 135 | 0 | 2 | 0 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 35.14 | 33 | 0 | 0 | 12 | 12 | 1.07 | 221 | 0 | 12 | 757 | 0 | 0 | 9 | 0 | 0 | 220 | 0 | 0 | 0 | 1030 | 6 | 51 | 85 | 184 | 0 | 347 | 246 | 43 | 195 | 34 | 62 | 50 | 66 | 45 | 20 | 44 | 40 | 0 | 50 | 42 | 17 | 300 | 332 | 0 | 60 | 145 | 8 | 0 | 80 | 30 | 0 | 16 | 0 | 17 | 75 | 45 | 69 | 1 | 36.45 | 12 | 7328.36 | 433 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17.89 | 957 | 0 | 1176 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 70 | 0 | 23.43 | 190 | 0 | 185 | 0 | 194 | 0 | 343 | 0 | 1.84 | 156 | 0 | 35 | 7 | 34 | 0 | 0 | 6.7 | 109 | 0.21 | 0 | 203 | 120 | 220 | 0 | 305 | 950 | 0 | 5988.07 | 13316.43 | 105.81
14:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.4 | 35 | 50 | 16 | 15 | 15 | 55 | 146 | 16 | 450 | 148 | 500 | 0 | 17 | 300 | 135 | 0 | 4 | 0 | 27.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19.28 | 33 | 0 | 0 | 12 | 12 | 3.12 | 221 | 0 | 11 | 760 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 950 | 6 | 51 | 130 | 184 | 0 | 317 | 340 | 45 | 195 | 34 | 68 | 50 | 92 | 47 | 20 | 32 | 38 | 0 | 32 | 42 | 14 | 295 | 331 | 0 | 58 | 133 | 4 | 0 | 82 | 30 | 0 | 16 | 0 | 17 | 75 | 45 | 69 | 0 | 42.78 | 12 | 7309.08 | 432 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24.18 | 980 | 0 | 1186.98 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 6.01 | 62 | 0 | 6.76 | 170 | 0 | 170 | 0 | 170 | 0 | 340 | 0 | 0.61 | 159 | 0 | 35 | 34 | 40 | 0 | 0 | 5 | 94 | 0.02 | 0 | 198 | 100 | 180 | 0 | 306 | 944 | 0 | 5894.56 | 13203.64 | 105.82
15:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.8 | 35 | 50 | 16 | 15 | 15 | 55 | 116 | 16 | 450 | 148 | 500 | 0 | 17 | 300 | 134 | 0 | 3 | 35 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5.32 | 33 | 0 | 0 | 12 | 12 | 1.62 | 221 | 0 | 6 | 763 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 950 | 5 | 51 | 110 | 177 | 0 | 300 | 340 | 44 | 195 | 34 | 65 | 70 | 95 | 52 | 20 | 32 | 42 | 0 | 24 | 42 | 14 | 290 | 332 | 0 | 60 | 135 | 4 | 0 | 82 | 30 | 0 | 16 | 0 | 17 | 96 | 65 | 69 | 1 | 11.11 | 12 | 7256.85 | 432 | 206 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 31.06 | 983 | 0 | 1116.44 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0.66 | 50 | 0 | 14.39 | 170 | 0 | 170 | 0 | 170 | 0 | 342 | 0 | 0.61 | 160 | 0 | 35 | 30 | 49 | 0 | 0 | 6 | 111 | 0.06 | 0 | 198 | 100 | 180 | 0 | 305 | 950 | 0 | 5856.22 | 13113.07 | 105.83
16:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 35 | 50 | 0 | 0 | 0 | 24 | 35 | 0 | 450 | 150 | 500 | 0 | 0 | 330 | 196 | 0 | 4 | 35 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 0.86 | 220 | 0 | 14 | 761 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 960 | 5 | 51 | 0 | 177 | 0 | 300 | 340 | 46 | 211 | 32 | 68 | 70 | 100 | 47 | 20 | 34 | 38 | 0 | 9 | 43 | 14 | 290 | 354 | 0 | 60 | 144 | 7 | 0 | 82 | 30 | 0 | 16 | 0 | 17 | 104 | 65 | 69 | 1 | 0.39 | 12 | 7063.25 | 432 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10.02 | 984 | 0 | 1083.37 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1.23 | 13 | 0 | 11.24 | 170 | 0 | 170 | 0 | 170 | 0 | 388 | 0 | 1.13 | 160 | 0 | 35 | 10 | 49 | 0 | 0 | 0.2 | 54 | 0.12 | 0 | 175 | 120 | 220 | 0 | 306 | 950 | 0 | 5768.31 | 12831.56 | 105.84
17:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.7 | 35 | 50 | 0 | 0 | 0 | 17 | 33 | 0 | 450 | 146 | 500 | 0 | 0 | 335 | 197 | 0 | 4 | 35 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 33 | 0 | 0 | 12 | 12 | 0 | 219 | 0 | 23 | 761 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 936 | 0 | 51 | 0 | 184 | 0 | 354 | 340 | 47 | 192 | 31 | 89 | 70 | 100 | 43 | 20 | 30 | 38 | 0 | 4 | 43 | 35 | 290 | 364 | 0 | 60 | 143 | 7 | 0 | 82 | 30 | 0 | 16 | 0 | 17 | 104 | 65 | 71 | 0 | 2.13 | 12 | 7120.83 | 431 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.88 | 915 | 0 | 1047.37 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1.93 | 1 | 0 | 4.91 | 170 | 0 | 170 | 0 | 170 | 0 | 336 | 0 | 0.54 | 190 | 0 | 35 | 5 | 49 | 0 | 0 | 2.3 | 59 | 0.1 | 0 | 166 | 120 | 220 | 0 | 304 | 950 | 0 | 5610.03 | 12730.86 | 105.85
18:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2 | 35 | 50 | 0 | 0 | 0 | 17 | 31 | 0 | 450 | 150 | 500 | 0 | 0 | 329 | 134 | 0 | 1 | 35 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 33 | 0 | 0 | 12 | 12 | 0.2 | 218 | 0 | 23 | 760 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 952 | 0 | 51 | 0 | 145 | 0 | 345 | 340 | 48 | 183 | 32 | 115 | 70 | 98 | 47 | 20 | 31 | 38 | 0 | 2 | 43 | 35 | 290 | 389 | 0 | 60 | 136 | 7 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 104 | 65 | 71 | 0 | 0.91 | 12 | 7051.31 | 432 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.88 | 886 | 0 | 964.68 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0.88 | 4 | 0 | 1.33 | 170 | 0 | 170 | 0 | 170 | 0 | 382 | 0 | 0.15 | 199 | 0 | 35 | 2 | 52 | 0 | 0 | 0.9 | 13 | 0.03 | 0 | 174 | 120 | 220 | 0 | 305 | 850 | 0 | 5409.85 | 12461.16 | 105.86
19:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 35 | 62 | 40 | 15 | 10 | 42 | 102 | 0 | 450 | 149 | 550 | 0 | 17 | 330 | 185 | 0 | 0 | 70 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 65 | 19 | 0 | 12 | 12 | 0 | 218 | 0 | 23 | 760 | 0 | 0 | 24 | 0 | 0 | 220 | 0 | 0 | 0 | 1179 | 0 | 51 | 40 | 86 | 0 | 314 | 300 | 48 | 208 | 32 | 115 | 70 | 100 | 55 | 20 | 32 | 42 | 0 | 0 | 43 | 45 | 290 | 396 | 0 | 60 | 140 | 7 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 104 | 85 | 72 | 0 | 0 | 12 | 7743 | 432 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1044 | 17 | 1172.08 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 198 | 0 | 198 | 0 | 400 | 0 | 0 | 199 | 0 | 88 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 120 | 220 | 0 | 306 | 950 | 0 | 6156.08 | 13899.08 | 105.87
19:30 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 35 | 88 | 47 | 15 | 15 | 55 | 100 | 8 | 450 | 141 | 550 | 0 | 17 | 333 | 197 | 0 | 0 | 90 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 65 | 30 | 0 | 12 | 12 | 0 | 218 | 0 | 27 | 756 | 0 | 0 | 32 | 0 | 0 | 220 | 0 | 0 | 0 | 1155 | 0 | 51 | 120 | 86 | 0 | 350 | 340 | 48 | 204 | 32 | 115 | 70 | 95 | 55 | 20 | 30 | 40 | 0 | 0 | 43 | 60 | 290 | 387 | 0 | 60 | 142 | 7 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 102 | 150 | 72 | 0 | 0 | 12 | 7910 | 432 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1144 | 17 | 1284.39 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 198 | 0 | 198 | 0 | 411 | 0 | 0 | 197 | 0 | 113 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 306 | 1080 | 0 | 6603.39 | 14513.39
20:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.3 | 35 | 88 | 47 | 15 | 15 | 55 | 99 | 16 | 450 | 140 | 550 | 0 | 17 | 335 | 198 | 0 | 0 | 90 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 65 | 32 | 0 | 12 | 12 | 0 | 218 | 0 | 31 | 756 | 0 | 0 | 33 | 0 | 0 | 221 | 0 | 0 | 0 | 1105 | 0 | 51 | 120 | 86 | 0 | 354 | 340 | 47 | 197 | 32 | 115 | 70 | 100 | 54 | 20 | 28 | 42 | 0 | 0 | 43 | 70 | 290 | 353 | 0 | 60 | 137 | 7 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 103 | 150 | 72 | 0 | 0 | 12 | 7819.3 | 433 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1167 | 17 | 1301.65 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 198 | 0 | 198 | 0 | 387 | 0 | 0 | 200 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 120 | 220 | 0 | 305 | 1110 | 0 | 6654.65 | 14473.95 | 105.88
21:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.5 | 35 | 86 | 31 | 15 | 15 | 55 | 94 | 16 | 450 | 141 | 500 | 0 | 17 | 335 | 198 | 0 | 0 | 90 | 23 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 65 | 32 | 0 | 12 | 12 | 0 | 219 | 0 | 31 | 758 | 0 | 0 | 23 | 0 | 0 | 220 | 0 | 0 | 0 | 1145 | 0 | 51 | 120 | 16 | 0 | 353 | 340 | 48 | 196 | 32 | 115 | 70 | 120 | 53 | 20 | 30 | 40 | 0 | 0 | 43 | 110 | 290 | 374 | 0 | 60 | 133 | 7 | 0 | 74 | 0 | 0 | 18 | 0 | 17 | 104 | 150 | 81 | 0 | 0 | 12 | 7878.5 | 432 | 205 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 17 | 1315.96 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 198 | 0 | 198 | 0 | 353 | 0 | 0 | 160 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 304 | 1110 | 0 | 6645.96 | 14524.46 | 105.89
22:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 88 | 15 | 0 | 0 | 44 | 72 | 19 | 450 | 143 | 490 | 0 | 17 | 333 | 198 | 0 | 0 | 90 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 65 | 32 | 0 | 12 | 12 | 0 | 219 | 0 | 32 | 757 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1140 | 0 | 51 | 30 | 16 | 0 | 354 | 340 | 48 | 194 | 32 | 114 | 50 | 120 | 53 | 20 | 30 | 42 | 0 | 0 | 43 | 160 | 290 | 361 | 0 | 60 | 132 | 7 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 104 | 150 | 80 | 0 | 0 | 12 | 7730 | 430 | 203 | 0 | 0 | 3 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 0 | 1321.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 198 | 0 | 198 | 0 | 346 | 0 | 0 | 162 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 120 | 220 | 0 | 305 | 1110 | 0 | 6565.4 | 14295.4 | 105.9
23:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 35 | 60 | 15 | 0 | 0 | 17 | 62 | 16 | 450 | 146 | 500 | 0 | 17 | 333 | 198 | 0 | 0 | 90 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 65 | 32 | 0 | 12 | 12 | 0 | 219 | 0 | 17 | 608 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1160 | 0 | 51 | 20 | 20 | 0 | 353 | 340 | 48 | 200 | 31 | 113 | 50 | 138 | 58 | 20 | 48 | 44 | 0 | 0 | 43 | 220 | 285 | 387 | 0 | 60 | 132 | 7 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 104 | 120 | 81 | 0 | 0 | 12 | 7596 | 430 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 1352.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 198 | 0 | 198 | 0 | 359 | 0 | 0 | 165 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 304 | 1111 | 0 | 6616.43 | 14212.43 | 105.91
Total KWH | 0 | 1445760 | 554400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298044 | 852840 | 1528128 | 220320 | 309873 | 93363 | 669338 | 1239840 | 96960 | 10302500 | 3559564 | 12144825 | 0 | 261387 | 7972849 | 4271000 | 0 | 51573 | 1275600 | 595200 | 499320 | 0 | 0 | 0 | 0 | 51840 | 0 | 481440 | 714446 | 225024 | 0 | 221760 | 228480 | 11641 | 5286400 | 0 | 505440 | 18014545.46 | 0 | 0 | 285120 | 11386.8 | 28436 | 5241549 | 0 | 0 | 0 | 24878179 | 40905 | 1204742 | 914981 | 3629818 | 0 | 8639400 | 4464000 | 1123680 | 4826000 | 815256 | 1806720 | 1196120 | 2623200 | 1299480 | 390510 | 1055640 | 938880 | 111624 | 264709 | 1030352 | 748540 | 7022600 | 9203000 | 0 | 1410720 | 3355281 | 176880 | 0 | 1837440 | 568800 | 0 | 416000 | 0 | 417960 | 2200800 | 2311200 | 1940160 | 6800 | 213310 | 290160 | 172924039.26 | 10418909 | 5227776 | 0 | 0 | 4224 | 912000 | 0 | 0 | 0 | 0 | 0 | 264960 | 24152720 | 48000 | 28248364 | 0 | 0 | 0 | 0 | 36768 | 0 | 214480 | 0 | 0 | 10643 | 317510 | 12285 | 135000 | 4823727 | 0 | 4809836 | 0 | 4850282 | 0 | 9101309 | 0 | 11880 | 4093000 | 0 | 1752063 | 187487 | 1881206 | 0 | 0 | 47596.32 | 1113120 | 2034 | 0 | 5520000 | 2837000 | 5033330 | 0 | 7351992 | 25530181.82 | 0 | 148949683.14 | 321873722.4

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 31-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13228.14 | MW | 12:00 Hr. | Energy Generated |  |  | 321.8737 |  | MKWHr.
| Day Peak Demand |  |  | 13228.14 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.424 |  | MKWHr.
| Evening Peak Generation |  |  | 14524.46 | MW | 21:00 Hr. | Energy Demand |  |  | 322.2977 |  | MKWHr.
| Evening Peak Demand |  |  | 14580.27 | MW | 19:30 Hr. | Maximum Temperature |  |  | 30.6 |  | °C
| Minimum Generation of the Day |  |  | 12264.32 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 992.88 |  | MMCFD
| Maximum Generation of the Day |  |  | 14760.6 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.0996 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.3453 | 0 | 8.8459 | 0 | 0 | 0.051573 | 0 | 0 | 48.2427 | Gas | 134.7445 | Gas | 494044887.92
| Chattogram Zone |  |  | 5.747 | 42.8927 | 1.7665 | 0 | 5.2864 | 0.052546 | 0 | 0.48144 | 56.2266 | Coal | 109.5406 | Coal | 657256283.8178
| Cumilla Zone |  |  | 26.2895 | 0 | 8.842 | 0 | 0 | 0.26471 | 0.93888 | 0 | 36.3351 | HFO | 28.6235 | HFO | 528074055.306
| Mymensingh Zone |  |  | 1.9402 | 0 | 5.2201 | 0 | 0 | 0.22011 | 0 | 0 | 7.3804 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 24.7393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.7393 | Hydro | 5.2864 | Hydro | 528640
| Khulna Zone |  |  | 5.2278 | 24.1527 | 0.052224 | 0 | 0 | 0.26496 | 11.3309 | 0 | 41.0286 | Solar | 2.6792 | Solar | 44901740.2652
| Barishal Zone |  |  | 7.8703 | 38.4022 | 0 | 0 | 0 | 0.002034 | 0 | 0 | 46.2745 | Import | 40.5182 | Import | 231438377.85
| Rajshahi Zone |  |  | 23.5852 | 0 | 0.26353 | 0 | 0 | 0.47503 | 28.2484 | 0 | 52.5721 | Wind | 0.48144 | Wind | 7048281.6
| Rangpur Zone |  |  | 0 | 4.093 | 3.6333 | 0 | 0 | 1.3482 | 0 | 0 | 9.0745
| Total |  |  | 134.7445 | 109.5406 | 28.6235 | 0 | 5.2864 | 2.6792 | 40.5182 | 0.48144 | 321.8737
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 494044887.92 |  | Hydro | 528640
|  |  |  | Coal | 657256283.8178 |  | Solar | 44901740.2652
|  |  |  | HFO | 528074055.306 |  | Import | 231438377.85
|  |  |  | HSD | 0 |  | Wind | 7048281.6
[5 empty] | Total: | 196,32,92,266 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 10.4189 | Peak Hr Flow | 432.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46888181.88 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.2484 | Peak Hr Flow | 1315.96 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 606 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.93888 | Peak Hr Flow | 40.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 930 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.6062 | Peak Hr Flow | 1787.96 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5015
|  |  |  | Chattogram |  | 0 |  | 1481
|  |  |  | Cumilla |  | 0 |  | 1344
|  |  |  | Mymensingh |  | 0 |  | 1149
|  |  |  | Sylhet |  | 0 |  | 520
|  |  |  | Khulna |  | 0 |  | 1572
|  |  |  | Barishal |  | 0 |  | 444
|  |  |  | Rajshahi |  | 0 |  | 1454
|  |  |  | Rangpur |  | 45 |  | 1037
|  |  |  | Total |  | 45 |  | 14016
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[7 empty] | 4 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222
[7 empty] | 5 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119
[7 empty] | 6 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 7 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 1048
|  |  |  | Total Unavailable Capacity |  |  |  | 1348
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:32 | 21:12 | Gopalganj 400/132kV S/S 400kV Rooppur Project Work S/D
|  | 09:38 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
|  | 09:39 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT is restored.
| 10:34 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 11:05 | 11:35 | Barapukuria-Saidpur 132 kV Ckt-2 Tripped from Saidpur 132/33kV end showing SOTF(in | [7 empty] | 59.0MW load
|  |  | distance) relays Due to Bad weather. | [7 empty] | interrup. Saidpur
132/33kV end
| 12:00 |  | Day peak Generation is 13225 MW
|  | 12:04 | Daudkandi 132/33kV S/S Transformer-2 HT is restored.
| 12:06 | 18:30 | Madunaghat 132/33kV S/S ATR-1(705T) LT Project Work S/D Due to SCADA Operation By Project
Work.
|  | 12:07 | Daudkandi 132/33kV S/S Transformer-2 LT is restored.
| 12:07 | 18:31 | Madunaghat 132/33kV S/S ATR-1(705T) HT Project Work S/D Due to SCADA operation by the
CNTIC Project Work.
| 12:45 | 20:05 | Lakshmipur 132/33kV S/S Transformer-2 LT Project Work S/D
| 18:58 |  | Shahjibazar 132/33kV S/S TR-06 LT Tripped showing No Relay relays Due to 33 kv habiganj
feeder breaker burn
| 18:58 |  | Shahjibazar 132/33kV S/S TR-06 HT Tripped showing Over Current Relay relays Due to 33 kv
habiganj feeder breaker burn
| 18:58 |  | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing Lockout Relay relays Due to 33 kv
habiganj feeder breaker burn
| 18:58 |  | Shahjibazar 132/33kV S/S TR-04 HT Tripped showing Lockout Relay, O/C, E/F relays Due to
33 kv habiganj feeder breaker burn
| 18:58 |  | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Lockout Relay relays.
| 18:58 |  | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing No Relay relays.
| 19:00 | 19:08 | Ashuganj 230/132/33kV S/S TR-OAT-11 LT Tripped showing Over Current, No.2 Master Trip
Relay relays.
| 19:00 | 19:06 | Ashuganj 230/132/33kV S/S TR-OAT-11 HT Tripped showing Over Current, No.2 Master Trip
Relay relays.
| 19:06 | 19:52 | Ashuganj-Shahjibazar 132kV Ckt-1 Forced S/D from Ashuganj 230/132/33kV end Due to Asper
instruction of NLDC
| 02:07 |  | Meghnaghat CCPP(Summit) GT-1 Planned Shutdown with remarks:- GT-1 shutdown as per NLDC
for PGCB substation maintenance work.
| 02:07 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT1
| 02:08 |  | Meghnaghat CCPP(Summit) ST Planned Shutdown with remarks:- None
| 02:22 |  | Summit Bibiana-2 CCPP tripped
| 03:50 |  | Meghnaghat CCPP(Summit) ST Ready with remarks:- None
| 03:50 |  | Meghnaghat CCPP(Summit) GT-1 Ready with remarks:- None
| 05:50 |  | Coxsbazar 132/33kV S/S Main Bus Project Work S/D Due to Patiya Grid substation | [7 empty] | 95.0MW load
|  |  | Commission. | [7 empty] | interrup.
| 06:14 |  | Dohazari-Sikalbaha 132 kV Ckt-1 Project Work S/D from Shikalbaha 230/132kV end.
| 06:14 |  | Dohazari-Sikalbaha 132 kV Ckt-2 Project Work S/D from Shikalbaha 230/132kV end.
| 06:15 |  | Keranigonj 230/132/33kV S/S ATR-2 LT Scheduled S/D Due to Red Hot Maintenance work at
R-phase of ATR-02
| 06:16 |  | Keranigonj 230/132/33kV S/S ATR-2 HT Scheduled S/D Due to Red Hot Maintenance Work at
R-phase
| 06:19 |  | Meghnaghat 230/132kV S/S Bus2 Scheduled S/D Due to Red hot problem.
| 07:00 |  | Minimum Generation 11270 MW
| 07:00 |  | Chowmuhani-Feni 132 kV Ckt-2 Scheduled S/D from Feni 132/33kV end Due to For red hot | [7 empty] | and 20.0MW load
|  |  | maintenance and from Chowmuhani 132/33kV end Due to 132 KV Bus Shutdown Feni End Sub | [7 empty] | interrup.
|  |  | Station | [7 empty] | Chowmuhani 132/33kV
end
| 07:01 |  | Madunaghat-TKCL 132kV Ckt-1 Project Work S/D from Madunaghat 132/33kV end Due to
Chittagong Waterlogging Removal Project of Chattogram City by the Bangladesh Army.
| 07:05 |  | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to For red hot
maintenance
| 07:06 |  | Baroirhat-Feni 132 kV Ckt-2 Scheduled S/D from Feni 132/33kV end Due to For red hot
maintenance and from Baroirhat 132/33kVend.
| 07:07 |  | Feni-PHP 132kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to For red hot maintenance
| 07:07 |  | Feni 132/33kV S/S Bus-2 Scheduled S/D Due to For Red hot maintenance
| 07:10 |  | Gulsan-Rampura 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to GIS IVT
change in Gulshan SS and from Gulshan 132/33kV end Due to IVT Replacement Work Gulshan
End.
| 07:10 |  | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Scheduled S/D Due to Condutor loop (B
Phase) Replace of CT to CB.
| 07:11 |  | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT Scheduled S/D Due to Condutor loop (B
Phase) Replace of CT to CB
| 07:14 |  | Meghnaghat-Shyampur 230kV Ckt-2 Scheduled S/D from Shyampur 230/132kV end Due to Red Hot
maintenance at Meghnaghat 400KV End. and from Meghnaghat 400/230kV end Due to Shutdown
for maintenance work.
| 07:18 |  | Madunaghat-Sikalbaha 132kV Ckt-2 Project Work S/D from Madunaghat 132/33kV end Due to
Chittagong Waterlogging Removal Project of Chattogram City by the Bangladesh Army.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 31-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10302500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 141 | 3559564 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 93363 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 198 | 4271000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7972849 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 45.5 | 298044 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 31 | 220320 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 669338 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 261387 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 595200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 6 | 499320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 554400 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 309873 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 86 | 1528128 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 87 | 1445760 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 96960 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 94 | 1239840 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 51573 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 852840 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 500 | 12144825 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 1275600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 2264.5 | 48242684
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 11386.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 40905 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 23 | 285120 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 219 | 5286400 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5241549 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 28436 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 32 | 225024 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 714446 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 221760 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 31 | 505440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 51840 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 11641 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 228480 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1145 | 24878179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 20 | 481440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 758 | 18014545.46 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2537 | 56226592.26
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 196 | 4826000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 353 | 8639400 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 4464000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 32 | 815256 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1123680 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 16 | 3629818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1204742 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 120 | 914981 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 1030352 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1196120 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 2623200 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 40 | 938880 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 111624 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 390510 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 30 | 1055640 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 53 | 1299480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1806720 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 264709 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1647 | 36335112
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 81 | 1940160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 150 | 2311200 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 2200800 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 213310 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 290160 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 417960 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 364 | 7380390
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1410720 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 133 | 3355281 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 568800 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 74 | 1837440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 416000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 7 | 176880 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 110 | 748540 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 374 | 9203000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 290 | 7022600 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2325 | 1066 | 24739261
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 432 | 10418909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 2 | 4224 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 205 | 5227776 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 48000 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 264960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1216 | 24152720 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1910 | 41028589
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 304 | 7351992 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2837000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1110 | 25530181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5033330 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 277 | 5520000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2034 | -
Barishal Area Total |  |  |  |  | 2236 | 2031 | 46274537.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 10643 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 203 | 4823727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 198 | 4809836 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 198 | 4850282 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 353 | 9101309 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 12285 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 214480 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 36768 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 11880 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1315.96 | 28248364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 135000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 317510 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 2317.96 | 52572084
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 4093000 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1881206 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47596.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1752063 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 187487 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1113120 | -
Rangpur Area Total |  |  |  |  | 950 | 387 | 9074472.32
Eastern Grid Total |  |  |  |  | 17401.505 | 7878.5 | 172924039.26
Western Grid Total |  |  |  |  | 10442.16 | 6645.96 | 148949683.14
National Grid Total |  |  |  |  | 27843.665 | 14524.46 | 321873722.4
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 31-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9508.67 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4462.7 | MW
i) Dhaka area |  |  | 5014.61 |  | MW | i) Khulna area |  |  |  | 1572 | MW
ii) Chattogram area |  |  | 1481.3 |  | MW | ii) Barishal area |  |  |  | 444.5 | MW
iii) Cumilla area |  |  | 1343.76 |  | MW | iii) Rajshahi area |  |  |  | 1454.2 | MW
iv) Mymensingh area |  |  | 1149 |  | MW | iv) Rangpur area |  |  |  | 992 | MW
v) Sylhet area |  |  | 520 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13971.37 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 6 | 20:00 | 67 | Hathazari | 76 | 19:00 | 133 | PHP | 8 | 01:00
2 | AKSML | 147.7 | 17:00 | 68 | Ishurdi | 75 | 19:30 | 134 | Pabna | 118 | 19:30
3 | Aftabnagar | 52 | 12:00 | 69 | Jaldhaka | 91 | 20:00 | 135 | Palashbari | 100 | 20:00
4 | Agargaon | 128 | 13:00 | 70 | Jamalpur | 124 | 00:00 | 136 | Panchagarh | 66 | 20:00
5 | Agrabad | 74 | 19:00 | 71 | Jashore | 124 | 19:30 | 137 | Patuakhali | 67 | 00:00
6 | Amnura | 27 | 00:00 | 72 | Jhenaidah | 114 | 19:30 | 138 | Payra | 32 | 22:00
7 | Ashuganj | 97 | 23:00 | 73 | Joydebpur | 142 | 19:30 | 139 | Postogola | 57 | 12:00
8 | BSRM | 207 | 01:00 | 74 | Joypurhat | 64 | 00:00 | 140 | Purbachal | 20 | 00:00
9 | Bagerhat | 77 | 19:30 | 75 | Juldah | 15.5 | 00:00 | 141 | Purbasadipur | 132 | 22:00
10 | Bajitpur | 87 | 00:00 | 76 | KSRM | 47 | 14:00 | 142 | Rahanpur | 41 | 23:00
11 | Bakulia | 82 | 13:00 | 77 | Kabirpur | 231 | 10:00 | 143 | Rahim | 22 | 12:00
12 | Banani | 86 | 12:00 | 78 | Kachua | 86 | 23:00 | 144 | Rajbari | 75 | 00:00
13 | Bangabhaban | 16 | 10:00 | 79 | Kallyanpur | 99 | 00:00 | 145 | Rajendrapur | 131 | 00:00
14 | Barapukuria | 66 | 19:30 | 80 | Kalurghat | 38 | 10:00 | 146 | Rajshahi | 106 | 00:00
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 75 | 00:00 | 147 | Rajshahi-230 | 86 | 13:00
16 | Barishal | 106 | 20:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 114 | 22:00
17 | Barishal-230 | 94 | 22:00 | 83 | Kasba | 34 | 00:00 | 149 | Rampur | 36 | 00:00
18 | Baroaulia | 63 | 15:00 | 84 | Kazla | 94 | 12:00 | 150 | Rangamati | 13 | 12:00
19 | Baroirhat | 66 | 00:00 | 85 | Keranigonj | 88 | 19:00 | 151 | Rangpur | 138 | 19:00
20 | Bashundhara | 190 | 12:00 | 86 | Khagrachori | 30 | 19:00 | 152 | Ruppur | 6.2 | 10:00
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 67 | 20:00 | 153 | SSM | 15 | 02:00
22 | Beanibazar | 78 | 02:00 | 88 | Khulshi | 181 | 15:00 | 154 | Saidpur | 109 | 12:00
23 | Benapole | 58 | 00:00 | 89 | Kishoreganj | 131 | 00:00 | 155 | Satkhira | 107 | 19:30
24 | Bhaluka | 155 | 00:00 | 90 | Kodda | 302 | 14:00 | 156 | Satmasjid | 93 | 13:00
25 | Bhandaria | 52 | 00:00 | 91 | Kulaura | 52 | 19:00 | 157 | Savar | 223 | 11:00
26 | Bhangura | 35 | 19:30 | 92 | Kurigram | 66 | 07:00 | 158 | SevenRings | 20.16 | 12:00
27 | Bheramara(GK) | 63 | 19:30 | 93 | Kushtia | 144 | 00:00 | 159 | ShahCement | 22 | 22:00
28 | Bhulta | 227 | 12:00 | 94 | Laksam | 32 | 00:00 | 160 | Shahjadpur | 73 | 19:00
29 | Bog-Sherpur | 68 | 00:00 | 95 | Lakshmipur | 21 | 21:00 | 161 | Shahjibazar | 128 | 00:00
30 | Bogura | 169 | 01:00 | 96 | Lalbag | 57 | 13:00 | 162 | Shahmirpur | 64 | 00:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 66 | 01:00 | 163 | Shariatpur | 84 | 22:00
32 | Brahmanbaria | 130 | 00:00 | 98 | MI_Cement | 13.8 | 10:00 | 164 | Sherpur | 152 | 00:00
33 | Cantonment | 128 | 19:00 | 99 | Madanganj | 40 | 00:00 | 165 | Shikalbaha | 20 | 00:00
34 | Chandina | 33.61 | 00:00 | 100 | Madaripur | 97 | 19:30 | 166 | Shitalakhya | 83.8 | 12:00
35 | Chandpur | 73 | 00:00 | 101 | Madartek | 91.26 | 00:00 | 167 | Sholosohor | 43 | 15:00
36 | Chandraghona | 34 | 19:00 | 102 | Madunaghat | 50 | 19:00 | 168 | Shyampur | 156 | 13:00
37 | Chapai | 68 | 00:00 | 103 | Magura | 59 | 19:30 | 169 | Siddhirganj | 116 | 12:00
38 | Charsaidpur | 43 | 02:00 | 104 | Mahasthangarh | 94 | 00:00 | 170 | Sirajganj | 102 | 00:00
39 | Chauddagram | 68 | 23:00 | 105 | Maijdee | 15 | 00:00 | 171 | Sonargaon | 115 | 23:00
40 | Chhatak | 42 | 22:00 | 106 | Manikganj | 117 | 19:30 | 172 | Sreemongol | 88 | 22:00
41 | Chowmuhani | 186 | 19:00 | 107 | Maniknagar | 78 | 13:00 | 173 | Sreepur | 107 | 12:00
42 | Chuadanga | 107 | 00:00 | 108 | Matarbari | 48 | 19:00 | 174 | Srinagar | 43.38 | 00:00
43 | Coxsbazar | 122 | 01:00 | 109 | Matuail | 66 | 12:00 | 175 | Sunamganj | 59 | 21:00
44 | Cumilla(N) | 134 | 22:00 | 110 | Millgate | 116 | 14:00 | 176 | Sylhet | 52 | 00:00
45 | Cumilla(S) | 148 | 15:00 | 111 | Mirpur | 135 | 12:00 | 177 | Sylhet-132 | 128 | 00:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 11:00 | 178 | TK | 33 | 23:00
47 | Daudkandi | 148 | 20:00 | 113 | Mirzapur | 44 | 00:00 | 179 | Tangail | 166 | 00:00
48 | Dhaka | 74 | 12:00 | 114 | Mithapukur | 70 | 19:30 | 180 | Taraganj | 26 | 00:00
49 | Dhamrai | 116 | 13:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 121 | 19:30
50 | Dhanmondi | 141 | 12:00 | 116 | Mogbazar | 145.2 | 12:00 | 182 | Tongi | 108 | 11:00
51 | Dohazari | 96 | 00:00 | 117 | Mongla | 38 | 10:00 | 183 | Ullahpara | 36 | 00:00
52 | Faridpur | 151 | 21:00 | 118 | Motijheel | 41 | 12:00 | 184 | Ullon | 39 | 00:00
53 | Fatullah | 98 | 11:00 | 119 | Muktagacha | 36 | 00:00 | 185 | Uttara | 81 | 12:00
54 | Fenchuganj | 43 | 22:00 | 120 | Munshiganj | 124.6 | 00:00 | 186 | UttaraNew | 60 | 00:00
55 | Feni | 102 | 00:00 | 121 | Muradnagar | 40 | 22:00 | 187 | Zigatola | 67 | 12:00
56 | GPH | 91 | 08:00 | 122 | Mymensingh | 193 | 19:00
57 | Ghatail | 80 | 00:00 | 123 | Naogaon | 126 | 00:00
58 | Ghorashal | 13 | 00:00 | 124 | Narail | 49 | 19:00
59 | Ghorashal-230 | 77 | 21:00 | 125 | Narinda | 74 | 12:00
60 | Goalpara | 30 | 12:00 | 126 | Narshingdi | 176 | 00:00
61 | Gollamari | 86 | 13:00 | 127 | Natore | 146 | 00:00
62 | Gopalganj | 100.6 | 19:30 | 128 | Nawabganj | 53.2 | 00:00
63 | Gulshan | 70 | 12:00 | 129 | Netrakona | 142 | 00:00
64 | Halishahar | 70 | 10:00 | 130 | New | 86 | 12:00
65 | HaripurSBU | 153 | 09:00 | 131 | Niamatpur | 73 | 00:00
66 | Hasnabad | 74 | 01:00 | 132 | Noapara | 36 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 31-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14760.6 | 79 |  | 14843.16
1:00 | 14315 | 72 |  | 14390.24
2:00 | 13919 | 20 |  | 13939.9
3:00 | 13462 | 0 |  | 13462
4:00 | 13120 | 0 |  | 13120
5:00 | 12905 | 0 |  | 12905
6:00 | 12288.94 | 0 |  | 12288.94
7:00 | 12264.32 | 0 |  | 12264.32
8:00 | 12390.52 | 0 |  | 12390.52
9:00 | 12368.74 | 0 |  | 12368.74
10:00 | 12620.95 | 0 |  | 12620.95
11:00 | 12926.28 | 0 |  | 12926.28
12:00 | 13228.14 | 0 |  | 13228.14
13:00 | 13316.43 | 17 |  | 13334.2
14:00 | 13203.64 | 0 |  | 13203.64
15:00 | 13113.07 | 0 |  | 13113.07
16:00 | 12831.56 | 0 |  | 12831.56
17:00 | 12730.86 | 0 |  | 12730.86
18:00 | 12461.16 | 0 |  | 12461.16
19:00 | 13899.08 | 0 |  | 13899.08
19:30 | 14513.39 | 64 |  | 14580.27
20:00 | 14473.95 | 74 |  | 14551.28
21:00 | 14524.46 | 45 |  | 14571.49
22:00 | 14295.4 | 43 |  | 14340.34
23:00 | 14212.43 | 74 |  | 14289.43
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 31-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7936.6 | 6824 | 14760.6 | DAILY GENERATION CURVE
00:30 | 7725.8 | 6812 | 14537.8
01:00 | 7515 | 6800 | 14315 | 31-07-2025
01:30 | 7371.5 | 6745.5 | 14117
02:00 | 7228 | 6691 | 13919
02:30 | 7066 | 6624.5 | 13690.5
03:00 | 6904 | 6558 | 13462
03:30 | 6838 | 6453 | 13291
04:00 | 6772 | 6348 | 13120
04:30 | 6700.5 | 6312 | 13012.5
05:00 | 6629 | 6276 | 12905
05:30 | 6504.66 | 6092.31 | 12596.97
06:00 | 6380.32 | 5908.62 | 12288.94
06:30 | 6416.675 | 5859.955 | 12276.63
07:00 | 6453.03 | 5811.29 | 12264.32
07:30 | 6511.485 | 5815.935 | 12327.42
08:00 | 6569.94 | 5820.58 | 12390.52
08:30 | 6533.85 | 5845.78 | 12379.63
09:00 | 6497.76 | 5870.98 | 12368.74
09:30 | 6578.15 | 5916.695 | 12494.845
10:00 | 6658.54 | 5962.41 | 12620.95
10:30 | 6749.75 | 6023.865 | 12773.615
11:00 | 6840.96 | 6085.32 | 12926.28
11:30 | 6917.925 | 6159.285 | 13077.21
12:00 | 6994.89 | 6233.25 | 13228.14
12:30 | 7161.625 | 6110.66 | 13272.285
13:00 | 7328.36 | 5988.07 | 13316.43
13:30 | 7318.72 | 5941.315 | 13260.035
14:00 | 7309.08 | 5894.56 | 13203.64
14:30 | 7282.965 | 5875.39 | 13158.355
15:00 | 7256.85 | 5856.22 | 13113.07
15:30 | 7160.05 | 5812.265 | 12972.315
16:00 | 7063.25 | 5768.31 | 12831.56
16:30 | 7092.04 | 5689.17 | 12781.21
17:00 | 7120.83 | 5610.03 | 12730.86
17:30 | 7086.07 | 5509.94 | 12596.01
18:00 | 7051.31 | 5409.85 | 12461.16
18:30 | 7397.155 | 5782.965 | 13180.12
19:00 | 7743 | 6156.08 | 13899.08
19:30 | 7910 | 6603.39 | 14513.39
20:00 | 7819.3 | 6654.65 | 14473.95
20:30 | 7848.9 | 6650.305 | 14499.205 |  | Executive Engineer
21:00 | 7878.5 | 6645.96 | 14524.46 |  | Network Operation Division
21:30 | 7804.25 | 6605.68 | 14409.93
22:00 | 7730 | 6565.4 | 14295.4
22:30 | 7663 | 6590.915 | 14253.915
23:00 | 7596 | 6616.43 | 14212.43

## En-Curve
QF-LDC-12
Date | 31-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3540 | 1939 | 428 | 38 | 46 | 1439 | 219 | 4885 | 0 | 484 | 1726.6 | 0 | 0 | 16 | 79 | DAILY ENERGY CURVE
00:30 | 3563.5 | 1940.5 | 428.5 | 38 | 45 | 1440.5 | 219.5 | 4917.5 | 0 | 415 | 1516.3 | 0 | 0 | 13.5 | 75.5 | 31-07-2025
01:00 | 3587 | 1942 | 429 | 38 | 44 | 1442 | 220 | 4950 | 0 | 346 | 1306 | 0 | 0 | 11 | 72
01:30 | 3596.5 | 1937.5 | 428.5 | 38 | 44 | 1430.5 | 220 | 4918.5 | 0 | 303 | 1191 | 0 | 0 | 9.5 | 46 | Energy Generated | 321.8737 |  | MKWHr
02:00 | 3606 | 1933 | 428 | 38 | 44 | 1419 | 220 | 4887 | 0 | 260 | 1076 | 0 | 0 | 8 | 20 | Energy not Served | 0.424 |  | MKWHr
02:30 | 3572.5 | 1930 | 428 | 38 | 43 | 1368 | 219.5 | 4806 | 0 | 240 | 1037 | 0 | 0 | 8.5 | 10 | Total Energy Requirement | 322.2977 |  | MKWHr
03:00 | 3539 | 1927 | 428 | 38 | 42 | 1317 | 219 | 4725 | 0 | 220 | 998 | 0 | 0 | 9 | 0
03:30 | 3529 | 1931.5 | 428 | 38 | 42 | 1295 | 219 | 4667 | 0 | 188 | 941.5 | 0 | 0 | 12 | 0
04:00 | 3519 | 1936 | 428 | 38 | 42 | 1273 | 219 | 4609 | 0 | 156 | 885 | 0 | 0 | 15 | 0
04:30 | 3540.5 | 1932.5 | 428 | 38 | 41 | 1273.5 | 218.5 | 4528.5 | 0 | 147 | 850 | 0 | 0 | 15 | 0
05:00 | 3562 | 1929 | 428 | 38 | 40 | 1274 | 218 | 4448 | 0 | 138 | 815 | 0 | 0 | 15 | 0
05:30 | 3519 | 1904.5 | 428 | 38 | 37 | 1217 | 217.5 | 4358 | 10.47 | 120.5 | 728 | 0 | 0 | 19 | 0
06:00 | 3476 | 1880 | 428 | 38 | 34 | 1160 | 217 | 4268 | 20.94 | 103 | 641 | 0 | 0 | 23 | 0
06:30 | 3508 | 1869 | 428 | 38 | 34 | 1114 | 217 | 4233 | 52.13 | 114.5 | 630.5 | 0 | 0 | 38.5 | 0
07:00 | 3540 | 1858 | 428 | 38 | 34 | 1068 | 217 | 4198 | 83.32 | 126 | 620 | 0 | 0 | 54 | 0
07:30 | 3553 | 1857.5 | 428 | 38 | 34 | 1072 | 217.5 | 4205.5 | 112.92 | 130.5 | 619 | 0 | 0 | 59.5 | 0
08:00 | 3566 | 1857 | 428 | 38 | 34 | 1076 | 218 | 4213 | 142.52 | 135 | 618 | 0 | 0 | 65 | 0
08:30 | 3585 | 1853.5 | 428 | 38 | 34 | 1077.5 | 218.5 | 4230.5 | 166.43 | 140 | 550 | 0 | 0 | 58.2 | 0
09:00 | 3604 | 1850 | 428 | 38 | 34 | 1079 | 219 | 4248 | 190.34 | 145 | 482 | 0 | 0 | 51.4 | 0
09:30 | 3664.5 | 1902.5 | 428 | 38 | 34 | 1077.5 | 219.5 | 4255 | 231.645 | 145 | 471 | 0 | 0 | 28.2 | 0
10:00 | 3725 | 1955 | 428 | 38 | 34 | 1076 | 220 | 4262 | 272.95 | 145 | 460 | 0 | 0 | 5 | 0
10:30 | 3724.5 | 1963 | 428.5 | 38 | 35 | 1091 | 220 | 4315.5 | 322.265 | 145 | 482 | 0 | 0 | 8.85 | 0
11:00 | 3724 | 1971 | 429 | 38 | 36 | 1106 | 220 | 4369 | 371.58 | 145 | 504 | 0 | 0 | 12.7 | 0
11:30 | 3737.5 | 1968.5 | 428.5 | 38 | 36 | 1139.5 | 220.5 | 4407.5 | 364.465 | 144 | 577.6 | 0 | 0 | 15.145 | 0
12:00 | 3751 | 1966 | 428 | 38 | 36 | 1173 | 221 | 4446 | 357.35 | 143 | 651.2 | 0 | 0 | 17.59 | 0
12:30 | 3678.5 | 1945 | 430.5 | 38 | 38 | 1174.5 | 221 | 4402 | 344.97 | 173 | 800.45 | 0 | 0 | 26.365 | 8.5
13:00 | 3606 | 1924 | 433 | 38 | 40 | 1176 | 221 | 4358 | 332.59 | 203 | 949.7 | 0 | 0 | 35.14 | 17
13:30 | 3575.5 | 1897.75 | 432.5 | 38 | 39 | 1181.49 | 221 | 4327.5 | 326.535 | 203 | 990.55 | 0 | 0 | 27.21 | 8.5
14:00 | 3545 | 1871.5 | 432 | 38 | 38 | 1186.98 | 221 | 4297 | 320.48 | 203 | 1031.4 | 0 | 0 | 19.28 | 0
14:30 | 3546.5 | 1866.25 | 432 | 38 | 40 | 1151.71 | 221 | 4303 | 304.995 | 216 | 1026.6 | 0 | 0 | 12.3 | 0
15:00 | 3548 | 1861 | 432 | 38 | 42 | 1116.44 | 221 | 4309 | 289.51 | 229 | 1021.8 | 0 | 0 | 5.32 | 0
15:30 | 3646 | 1893 | 432 | 38 | 40 | 1099.905 | 220.5 | 4302.5 | 205.35 | 211.5 | 880.9 | 0 | 0 | 2.66 | 0
16:00 | 3744 | 1925 | 432 | 38 | 38 | 1083.37 | 220 | 4296 | 121.19 | 194 | 740 | 0 | 0 | 0 | 0
16:30 | 3744 | 1941 | 431.5 | 38 | 38 | 1065.37 | 219.5 | 4259 | 106.99 | 194 | 739.35 | 0 | 0 | 4.5 | 0
17:00 | 3744 | 1957 | 431 | 38 | 38 | 1047.37 | 219 | 4222 | 92.79 | 194 | 738.7 | 0 | 0 | 9 | 0
17:30 | 3737.5 | 1934.5 | 431.5 | 38 | 38 | 1006.025 | 218.5 | 4174 | 61.035 | 194 | 752.95 | 0 | 0 | 10 | 0
18:00 | 3731 | 1912 | 432 | 38 | 38 | 964.68 | 218 | 4126 | 29.28 | 194 | 767.2 | 0 | 0 | 11 | 0
18:30 | 3779 | 1914 | 432 | 38 | 40 | 1068.38 | 218 | 4411 | 14.64 | 291.5 | 947.6 | 0 | 0 | 26 | 0
19:00 | 3827 | 1916 | 432 | 38 | 42 | 1172.08 | 218 | 4696 | 0 | 389 | 1128 | 0 | 0 | 41 | 0
19:30 | 3911 | 1847 | 432 | 38 | 40 | 1284.39 | 218 | 4917 | 0 | 437 | 1366 | 0 | 0 | 23 | 64
20:00 | 3855 | 1832 | 433 | 38 | 42 | 1301.65 | 218 | 4914 | 0 | 439 | 1388.3 | 0 | 0 | 13 | 74
20:30 | 3849.5 | 1831 | 432.5 | 38 | 41 | 1308.805 | 218.5 | 4942 | 0 | 432 | 1389.4 | 0 | 0 | 16.5 | 59.5
21:00 | 3844 | 1830 | 432 | 38 | 40 | 1315.96 | 219 | 4970 | 0 | 425 | 1390.5 | 0 | 0 | 20 | 45
21:30 | 3820.5 | 1863 | 431 | 38 | 41 | 1318.68 | 219 | 4963 | 0 | 392.5 | 1300.25 | 0 | 0 | 23 | 44
22:00 | 3797 | 1896 | 430 | 38 | 42 | 1321.4 | 219 | 4956 | 0 | 360 | 1210 | 0 | 0 | 26 | 43
22:30 | 3813.5 | 1927 | 430 | 38 | 43 | 1336.915 | 219 | 4899.5 | 0 | 358.5 | 1166 | 0 | 0 | 22.5 | 58.5
23:00 | 3830 | 1958 | 430 | 38 | 44 | 1352.43 | 219 | 4843 | 0 | 357 | 1122 | 0 | 0 | 19 | 74
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 31-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 07:00 | 371 | 12:00 | Payra | 415 | 08:00 | 410 | 21:00
Ashuganj | 405 | 5:00 | 378 | 11:00 | Rahanpur | 401 | 17:00 | 385 | 00:00
Bhulta | 402 | 05:00 | 377 | 12:00 | Rampal | 406 | 08:00 | 393 | 19:30
Bibiana | 386 | 18:00 | 378 | 11:00
BIPTC | 409 | 06:00 | 400 | 21:00
Bogura | 383 | 18:00 | 362 | 01:00
Gopalganj | 398 | 06:00 | 388 | 19:30
Kaliakoir | 375 | 07:00 | 363 | 12:00
Madunaghat | 391 | 08:00 | 384 | 12:00
Meghnaghat | 387 | 06:00 | 374 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 06:00 | 214 | 12:00 | Keranigonj | 221 | 06:00 | 212 | 12:00
AKSML | 228 | 07:00 | 221 | 12:00 | Khulna(S) | 231 | 06:00 | 220 | 19:30
Aminbazar | 224 | 05:00 | 215 | 12:00 | Madunaghat | 230 | 00:00 | 226 | 11:00
Ashuganj | 231 | 06:00 | 223 | 10:00 | Madunaghat-400 | 230 | 07:00 | 226 | 12:00
Ashuganj-400 | 231 | 06:00 | 223 | 10:00 | Maniknagar | 218 | 05:00 | 210 | 12:00
Baghabari | 235 | 17:00 | 226 | 23:00 | Meghnaghat | 225 | 07:00 | 219 | 11:00
Barapukuria | 222 | 17:00 | 215 | 00:00 | Meghnaghat-400 | 223 | 06:00 | 215 | 12:00
Barapukuria-230 | 222 | 17:00 | 215 | 00:00 | Mirsorai | 225 | 08:00 | 217 | 12:00
Barishal | 229 | 07:00 | 222 | 19:30 | Rajshahi | 233 | 18:00 | 220 | 00:00
Bheramara | 234 | 02:00 | 224 | 23:00 | Rampal | 230 | 05:00 | 221 | 21:00
Bhulta | 232 | 05:00 | 211 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 06:00 | 220 | 12:00 | Rampura | 230 | 05:00 | 214 | 12:00
BIPTC | 235 | 02:00 | 223 | 23:00 | Shikalbaha | 228 | 06:00 | 222 | 11:00
Bogura | 237 | 17:00 | 226 | 01:00 | Shyampur | 220 | 05:00 | 212 | 12:00
Bogura-400 | 237 | 18:00 | 226 | 22:00 | Siddhirganj | 221 | 07:00 | 212 | 11:00
Borhanuddin | 234 | 05:00 | 229 | 00:00 | Sirajgonj | 240 | 09:00 | 235 | 22:00
BSRM | 224 | 08:00 | 218 | 01:00 | Sreepur | 230 | 18:30 | 221 | 12:00
Cumilla(N) | 222 | 07:00 | 214 | 11:00 | Tongi | 226 | 07:00 | 215 | 11:00
Faridpur | 227 | 06:00 | 220 | 00:00
Fenchuganj | 227 | 18:00 | 221 | 02:00
Ghorashal | 235 | 01:00 | 225 | 10:00
Ghorashal-230 | 228 | 05:00 | 215 | 12:00
Gopalganj | 229 | 09:00 | 221 | 19:30
GPH | 226 | 08:00 | 221 | 12:00
Haripur | 220 | 07:00 | 211 | 12:00
Hasnabad | 221 | 03:00 | 214 | 10:00
Hathazari | 226 | 00:00 | 218 | 12:00
Ishurdi | 236 | 05:00 | 225 | 23:00
Jhenaidah | 230 | 05:00 | 218 | 22:00
Kaliakoir | 230 | 05:00 | 221 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 140 | 05:00 | 126 | 12:00 | Lalmonirhat | 129 | 19:30 | 120 | 01:00
Agargaon | 132 | 06:00 | 124 | 12:00 | Madanganj | 128 | 07:00 | 122 | 11:00
Agrabad | 129 | 00:00 | 124 | 12:00 | Madaripur | 134 | 08:00 | 130 | 00:00
AKS | 127 | 00:00 | 123 | 05:00 | Madartek | 139 | 05:00 | 126 | 12:00
Aminbazar | 131 | 03:00 | 125 | 12:00 | Madunaghat | 130 | 00:00 | 128 | 10:00
Amnura | 135 | 10:00 | 129 | 00:00 | Magura | 133 | 15:00 | 123 | 23:00
Ashuganj | 140 | 05:00 | 136 | 12:00 | Mahasthangarh | 137 | 18:00 | 127 | 01:00
Bagerhat | 133 | 17:00 | 121 | 22:00 | Maijdee | 118 | 18:00 | 111 | 16:00
Bajitpur | 131 | 04:00 | 125 | 22:00 | Manikganj | 128 | 06:00 | 121 | 12:00
Bakulia | 130 | 00:00 | 127 | 11:00 | Maniknagar | 132 | 05:00 | 125 | 12:00
Banani | 140 | 05:00 | 126 | 12:00 | Matarbari | 124 | 09:00 | 113 | 05:00
Bangabhaban | 133 | 06:00 | 125 | 12:00 | Matuail | 128 | 07:00 | 123 | 12:00
Barapukuria | 135 | 17:00 | 129 | 13:00 | Millgate | 132 | 00:00 | 123 | 12:00
Barguna | 134 | 05:00 | 130 | 00:00 | Mirpur | 132 | 00:00 | 124 | 12:00
Barishal | 133 | 06:00 | 127 | 23:00 | Mirzapur | 130 | 06:00 | 124 | 19:00
Barishal-230 | 134 | 06:00 | 128 | 21:00 | Mithapukur | 128 | 17:00 | 116 | 00:00
Baroaulia | 130 | 18:00 | 127 | 11:00 | MI_Cement | 129 | 07:00 | 123 | 11:00
Baroirhat | 122 | 08:00 | 115 | 22:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 138 | 03:00 | 124 | 12:00 | Mogbazar | 142 | 05:00 | 129 | 12:00
BashundharaCement | 128 | 07:00 | 122 | 11:00 | Mongla | 133 | 17:00 | 123 | 22:00
Beanibazar | 125 | 18:00 | 117 | 02:00 | Motijheel | 135 | 05:00 | 125 | 12:00
Benapole | 133 | 15:00 | 122 | 23:00 | Muktagacha | 135 | 17:00 | 128 | 19:00
Bhaluka | 132 | 06:00 | 126 | 00:00 | Munshiganj | 128 | 18:30 | 122 | 12:00
Bhandaria | 130 | 08:00 | 120 | 22:00 | Muradnagar | 126 | 07:00 | 119 | 19:00
Bhangura | 135 | 18:30 | 129 | 21:00 | Mymensingh | 136 | 10:00 | 117 | 22:00
Bheramara | 137 | 02:00 | 132 | 23:00 | Naogaon | 135 | 17:00 | 125 | 00:00
Bheramara(GK) | 137 | 05:00 | 132 | 23:00 | Narail | 133 | 09:00 | 122 | 22:00
Bhulta | 123 | 08:00 | 117 | 12:00 | Narinda | 132 | 05:00 | 125 | 12:00
Bog-Sherpur | 137 | 18:00 | 129 | 22:00 | Narshingdi | 136 | 18:30 | 118 | 12:00
Bogura | 139 | 18:00 | 132 | 00:00 | Natore | 135 | 17:00 | 127 | 23:00
Bogura-230 | 140 | 18:00 | 132 | 01:00 | Nawabganj | 132 | 06:00 | 125 | 12:00
Brahmanbaria | 135 | 05:00 | 129 | 01:00 | Netrakona | 127 | 06:00 | 115 | 00:00
Cantonment | 131 | 04:00 | 124 | 12:00 | New | 134 | 20:00 | 125 | 12:00
Chandina | 127 | 03:00 | 121 | 12:00 | Niamatpur | 137 | 18:00 | 130 | 00:00
Chandpur | 126 | 18:00 | 114 | 11:00 | Noapara | 135 | 06:00 | 126 | 22:00
Chandraghona | 131 | 06:00 | 128 | 12:00 | Pabna | 135 | 18:30 | 129 | 22:00
Chapai | 136 | 18:00 | 128 | 23:00 | Palashbari | 128 | 18:00 | 114 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 07:00 | 122 | 12:00 | Panchagarh | 132 | 03:00 | 119 | 13:00
Chauddagram | 122 | 07:00 | 115 | 12:00 | Patuakhali | 135 | 07:00 | 132 | 00:00
Chhatak | 123 | 06:00 | 113 | 19:00 | Payra | 136 | 05:00 | 133 | 00:00
Chowmuhani | 119 | 18:00 | 109 | 22:00 | PHP | 121 | 08:00 | 114 | 19:30
Chuadanga | 133 | 17:00 | 123 | 21:00 | Postogola | 130 | 06:00 | 124 | 12:00
Coxsbazar | 121 | 07:00 | 113 | 23:00 | Purbachal | 139 | 04:00 | 124 | 12:00
Cumilla(N) | 127 | 07:00 | 121 | 11:00 | Purbasadipur | 129 | 03:00 | 119 | 09:00
Cumilla(S) | 133 | 18:30 | 119 | 11:00 | Rahanpur | 139 | 01:00 | 131 | 00:00
Daganbhuiyan | 119 | 08:00 | 111 | 21:00 | Rahanpur-400 | 138 | 17:00 | 132 | 00:00
Daudkandi | 125 | 07:00 | 117 | 19:00 | Rahim | 128 | 06:00 | 124 | 11:00
Dhaka | 139 | 04:00 | 126 | 12:00 | Rajbari | 133 | 06:00 | 128 | 00:00
Dhamrai | 131 | 03:00 | 124 | 12:00 | Rajendrapur | 131 | 18:30 | 121 | 12:00
Dhanmondi | 140.6 | 05:00 | 126 | 12:00 | Rajshahi | 134 | 18:00 | 126 | 23:00
Dohazari | 128 | 08:00 | 123 | 11:00 | Rajshahi-230 | 134 | 18:30 | 126 | 23:00
Faridpur | 135 | 07:00 | 130 | 00:00 | Ramganj | 119 | 18:00 | 110 | 11:00
Fatullah | 130 | 07:00 | 117 | 01:00 | Rampur | 130 | 07:00 | 125 | 11:00
Fenchuganj | 133 | 07:00 | 128 | 01:00 | Rampura | 139 | 05:00 | 127 | 12:00
Feni | 123 | 08:00 | 112 | 22:00 | Rangamati | 130 | 02:00 | 127 | 12:00
Ghatail | 130 | 17:00 | 125 | 19:00 | Rangpur | 130 | 20:00 | 123 | 09:00
Ghorashal | 137 | 01:00 | 130 | 10:00 | Ruppur | 137 | 05:00 | 132 | 22:00
Goalpara | 138 | 06:00 | 128 | 22:00 | Saidpur | 130 | 18:30 | 118 | 13:00
Gollamari | 137 | 06:00 | 129 | 23:00 | Satkhira | 134 | 06:00 | 124 | 22:00
Gopalganj | 135 | 06:00 | 128 | 21:00 | Satmasjid | 131 | 07:00 | 124 | 12:00
Gopalganj-400 | 136 | 06:00 | 132 | 19:30 | Savar | 132 | 18:30 | 124 | 10:00
Gulshan | 137 | 00:00 | 127 | 12:00 | SevenRings | 137 | 05:00 | 128 | 12:00
Halishahar | 131 | 18:30 | 125 | 11:00 | ShahCement | 129 | 07:00 | 122 | 12:00
Haripur | 129 | 05:00 | 123 | 12:00 | Shahjadpur | 137 | 07:00 | 134 | 19:00
HaripurSBU | 129 | 04:00 | 123 | 12:00 | Shahjibazar | 135 | 15:00 | 128 | 00:00
Hasnabad | 131 | 05:00 | 124 | 11:00 | Shahmirpur | 131 | 00:00 | 126 | 11:00
Hathazari | 131 | 18:00 | 129 | 12:00 | Shariatpur | 134 | 07:00 | 127 | 21:00
Ishurdi | 138 | 05:00 | 132 | 23:00 | Sherpur | 137 | 11:00 | 128 | 13:00
Jaldhaka | 126 | 05:00 | 118 | 13:00 | Shikalbaha | 121 | 00:00 | 116 | 12:00
Jamalpur | 139 | 17:00 | 131 | 14:00 | Shikalbaha-230 | 132 | 08:00 | 128 | 11:00
Jashore | 132 | 17:00 | 122 | 22:00 | Shitalakhya | 129 | 07:00 | 123 | 11:00
Jhenaidah | 136 | 15:00 | 124 | 23:00 | Sholosohor | 130 | 08:00 | 126 | 12:00
Jhenaidah-230 | 136 | 17:00 | 127 | 21:00 | Shyampur | 128 | 00:00 | 123 | 12:00
Joydebpur | 138 | 06:00 | 125 | 12:00 | Shyampur-230 | 129 | 05:00 | 123 | 12:00
Joypurhat | 134 | 17:00 | 123 | 00:00 | Siddhirganj | 135 | 10:00 | 124 | 11:00
Juldah | 130 | 00:00 | 126 | 11:00 | Sirajganj | 134 | 18:30 | 127 | 22:00
Kabirpur | 131 | 04:00 | 121 | 12:00 | Sonargaon | 127 | 07:00 | 121 | 12:00
Kachua | 124 | 18:00 | 115 | 11:00 | Sreemongol | 132 | 14:00 | 122 | 19:00
Kaliakoir | 133 | 18:00 | 128 | 12:00 | Sreepur | 134 | 18:30 | 127 | 12:00
Kallyanpur | 131 | 19:30 | 126 | 10:00 | Srinagar | 133 | 06:00 | 126 | 12:00
Kalurghat | 130 | 00:00 | 127 | 12:00 | SSM | 133 | 00:00 | 130 | 11:00
Kamrangirchar | 133 | 07:00 | 125 | 12:00 | Sunamganj | 120 | 04:00 | 112 | 21:00
Kaptai | 131 | 6:00 | 123 | 12:00 | Sylhet | 125 | 08:00 | 118 | 02:00
Kasba | 125 | 08:00 | 118 | 19:30 | Sylhet-132 | 126 | 18:00 | 118 | 19:00
Kazla | 132 | 05:00 | 125 | 12:00 | Tangail | 128 | 17:00 | 124 | 00:00
Keranigonj | 133 | 06:00 | 126 | 12:00 | Taraganj | 128 | 04:00 | 120 | 04:00
Khagrachori | 130 | 00:00 | 127 | 02:00 | Thakurgaon | 131 | 03:00 | 118 | 13:00
Khulna | 135 | 08:00 | 127 | 22:00 | TK | 131 | 01:00 | 127 | 12:00
Khulna(S) | 137 | 06:00 | 129 | 22:00 | Tongi | 135 | 07:00 | 127 | 11:00
Khulshi | 128 | 00:00 | 124 | 11:00 | Ullahpara | 135 | 18:00 | 130 | 20:00
Kishoreganj | 129 | 17:00 | 122 | 22:00 | Ullon | 139 | 05:00 | 127 | 12:00
Kodda | 131 | 20:00 | 120 | 12:00 | Uttara | 130 | 05:00 | 124 | 12:00
KSRM | 131 | 18:00 | 126 | 12:00 | UttaraNew | 130 | 00:00 | 123 | 12:00
Kulaura | 132 | 18:30 | 126 | 19:00 | Zigatola | 133 | 06:00 | 123 | 18:00
Kurigram | 130 | 20:00 | 122 | 01:00
Kushtia | 134 | 06:00 | 127 | 23:00
Laksam | 123 | 18:00 | 114 | 11:00
Lakshmipur | 120 | 18:00 | 110 | 21:00
Lalbag | 133 | 07:00 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division