## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-08-2026 | during | 08-08-2026 | during | 08-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 325 | 325 | 412 | 412 | 300 | 300 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 120 | 120 | 335 | 335 | 120 | 120 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 270 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 5 | 54 | 53.97 | 53.97 | 0 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 111 | 143 | 149.36 | 149.36 | 125 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 3 | 35 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16 | 13 | 33 | 33 | 18 | 18 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 50 | 52.19 | 52.19 | 33 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 73 | 81 | 300 | 300 | 81 | 81 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 68 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 45 | 105 | 105 | 105 | 17 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 144 | 162 | 162 | 17 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 20 | 0 | 20 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 325 | 315 | 583 | 583 | 300.03 | 300.03 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1583.42 | 1960.42 | 5798.16 | 5778.16 | 1631.45 | 2029.45
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 8 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 2 | 0 | 3 | 0 | 3 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 220 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 186 | 186 | 140 | 140 | 140 | 140 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 27 | 99 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 23 | 24 | 24 | 24 | 24 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 34 | 25 | 30 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 43 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.5 | 0 | 2.39 | 0 | 2.39 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 17 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 25 | 106 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 7 | 92 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 8 | 152 | 163 | 163 | 16 | 83 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1190 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 38 | 25 | 21 | 25 | 21 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 795 | 1125 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2588.5 | 3510.36 | 4047.25 | 4093.86 | 3237.39 | 3427
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 353 | 356 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 342.01 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 33 | 41.65 | 41.65 | 34 | 34 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 43 | 44 | 52.82 | 52.82 | 44 | 44 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 108 | 180 | 195 | 195 | 110 | 110 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 10 | 50 | 150 | 150 | 50 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 16 | 14 | 24 | 24 | 24 | 24 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 50 | 163 | 163 | 0 | 0 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 95 | 178 | 200 | 200 | 80 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 148 | 164 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 6 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 24.5 | 24.5 | 8 | 8 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 105 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 13 | 88 | 115 | 115 | 51 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 31 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1018 | 1396 | 2495.19 | 2459.19 | 1156.21 | 1374.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-08-2026 | during | 08-08-2026 | during | 08-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 9.1 | 0 | 10 | 0 | 10 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.9 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 154 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.2 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 259.2 | 251 | 523.6 | 516.5 | 266.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 40 | 41 | 41 | 41 | 41 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 39 | 40 | 40 | 40 | 40 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 146 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 22 | 63 | 86 | 86 | 22.04 | 22.04 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 103 | 100 | 102 | 102 | 102 | 102 | plant availability zero
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 237 | 305 | 250 | 260 | 250 | 260 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 923 | 1011 | 1081 | 1091 | 917.04 | 927.04
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 901 | 901 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 27 | 30 | 30 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 37 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1162 | 1161 | 1165 | 1165 | 1165 | 1165 | AGC+FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2138 | 2142 | 3070 | 3005 | 2315 | 2250
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 600 | 1050 | 600 | 600 | 600 | 600 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 60 | 60 | 100 | 100 | 100 | 100 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 403 | 570 | 581.53 | 581.53 | 400 | 400 | Coal shortage
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 202 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.02 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1566.02 | 2153 | 2069.53 | 2068.53 | 1661 | 1660
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 57.08 | 0 | 48.25 | 0 | 48.25 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 175 | 175 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 280 | 377 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 14 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 7 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 0 | 0 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 25 | 100 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 57 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 2.56 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1206.16 | 805.4 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 19.77 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 94 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1901.57 | 1708.6 | 3117.87 | 2903.12 | 2404.49 | 2346.74
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 47 | 50 | 50 | 52 | 52 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 161 | 160 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 89 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.8 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 75 | 106 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 26 | 0 | 26 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 199 | 0 | 184.43 | 0 | 184.43 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 522.8 | 402 | 685.43 | 472 | 574.43 | 396
System Total |  |  |  |  | 28843.2 | 29171.687 | 12500.51 | 14534.38 | 22888.03 | 22387.36 | 14163.11 | 14669.44
Forecast Scenario (08-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14200 |  | 1633.05 |  | 15910
|  |  |  | 1:00 | 13830 |  | 1499.35 |  | 15400
|  |  |  | 2:00 | 13380 |  | 1528 |  | 14980
|  |  |  | 3:00 | 12970 |  | 1489.8 |  | 14530
|  |  |  | 4:00 | 12930 |  | 1251.05 |  | 14240
|  |  |  | 5:00 | 12670 |  | 1308.35 |  | 14040
|  |  |  | 6:00 | 12230 |  | 1356.1 |  | 13650
|  |  |  | 7:00 | 12040 |  | 1528 |  | 13640
|  |  |  | 8:00 | 12690 |  | 1012.3 |  | 13750
|  |  |  | 9:00 | 12910 |  | 1231.95 |  | 14200
|  |  |  | 10:00 | 12840 |  | 1403.85 |  | 14310
|  |  |  | 11:00 | 12910 |  | 1547.1 |  | 14530
|  |  |  | 12:00 | 13070 |  | 2015.05 |  | 15180
|  |  |  | 13:00 | 13080 |  | 2244.25 |  | 15430
|  |  |  | 14:00 | 13030 |  | 2301.55 |  | 15440
|  |  |  | 15:00 | 12970 |  | 2406.6 |  | 15490
|  |  |  | 16:00 | 12960 |  | 2349.3 |  | 15420
|  |  |  | 17:00 | 12830 |  | 1967.3 |  | 14890
|  |  |  | 18:00 | 13180 |  | 1394.3 |  | 14640
|  |  |  | 18:30 | 13150 |  | 2129.65 |  | 15380
|  |  |  | 19:00 | 13210 |  | 2588.05 |  | 15920
|  |  |  | 19:30 | 14360 |  | 2387.5 |  | 16860
|  |  |  | 20:00 | 14320 |  | 2425.7 |  | 16860
|  |  |  | 21:00 | 14540 |  | 2234.7 |  | 16880
|  |  |  | 22:00 | 14540 |  | 2053.25 |  | 16690
|  |  |  | 23:00 | 13460 |  | 3084.65 |  | 16690
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 15180.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2235
Probable Maximum Demand at Evening Peak: |  |  | 16880.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14540.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 316.79 MKWHr. |  | 325 | 195 | 315 | 300 | 150 | 350 | 130 | 250 | 220 | 2235
*** This report is generated digitally from Operation Information System (OIS) at 10:33 hrs on 08-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12500.51 | MW | 12:00 Hr. | Energy Generated |  |  | 343.36 |  | MKWHr.
| Day Peak Demand |  |  | 12541.27 | MW | 12:00 Hr. | Energy Unserverd |  |  | 18.041 |  | MKWHr.
| Evening Peak Generation |  |  | 14534.38 | MW | 21:00 Hr. | Energy Demand |  |  | 361.401 |  | MKWHr.
| Evening Peak Demand |  |  | 15623.38 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.2 |  | °C
| Minimum Generation of the Day |  |  | 11539.62 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 664.63 |  | MMCFD
| Maximum Generation of the Day |  |  | 14536.52 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 7.475 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.133 | 0 | 13.519 | 0 | 0 | 0.18602 | 0 | 0 | 39.838 | Gas | 90.2774 | Gas | 316679900.64
| Chattogram Zone |  |  | 4.8796 | 49.4818 | 10.2925 | 0 | 5.3185 | 0.051511 | 0 | 0.52224 | 70.5462 | Coal | 118.0902 | Coal | 808334223.6799
| Cumilla Zone |  |  | 16.0433 | 0 | 8.0846 | 0 | 0 | 0.2323 | 34.4426 | 0 | 58.8027 | HFO | 42.066 | HFO | 773372628.812
| Mymensingh Zone |  |  | 0 | 0 | 4.3223 | 0 | 0 | 0.4345 | 0 | 0 | 4.7568 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.0409 | 0 | 0 | 0 | 0 | 0.070349 | 0 | 0 | 23.1112 | Hydro | 5.3185 | Hydro | 531848.7
| Khulna Zone |  |  | 0 | 27.6655 | 0.17707 | 0 | 0 | 0.25704 | 22.4676 | 0 | 50.5672 | Solar | 4.1082 | Solar | 67841132.4852
| Barishal Zone |  |  | 6.9233 | 35.819 | 0.79224 | 0 | 0 | 0.001326 | 0 | 0 | 43.5358 | Import | 82.9773 | Import | 592160321.49
| Rajshahi Zone |  |  | 13.2574 | 0 | 2.3853 | 0 | 0 | 1.2213 | 26.0671 | 0 | 42.9311 | Wind | 0.52224 | Wind | 7682150.4
| Rangpur Zone |  |  | 0 | 5.124 | 2.493 | 0 | 0 | 1.6539 | 0 | 0 | 9.2709
| Total |  |  | 90.2774 | 118.0902 | 42.066 | 0 | 5.3185 | 4.1082 | 82.9773 | 0.52224 | 343.36
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 316679900.64 |  | Hydro | 531848.7
|  |  |  | Coal | 808334223.6799 |  | Solar | 67841132.4852
|  |  |  | HFO | 773372628.812 |  | Import | 592160321.49
|  |  |  | HSD | 0 |  | Wind | 7682150.4
[5 empty] | Total: | 256,66,02,206 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5556 | Peak Hr Flow | 901.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44765618.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.0671 | Peak Hr Flow | 805.40 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1705 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 34.4426 | Peak Hr Flow | 164.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2375 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 82.0653 | Peak Hr Flow | 1870.40 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 70 |  | 5069
|  |  |  | Chattogram |  | 0 |  | 1410
|  |  |  | Cumilla |  | 159 |  | 1538
|  |  |  | Mymensingh |  | 194 |  | 1355
|  |  |  | Sylhet |  | 88 |  | 712
|  |  |  | Khulna |  | 146 |  | 1783
|  |  |  | Barishal |  | 44 |  | 466
|  |  |  | Rajshahi |  | 220 |  | 1606
|  |  |  | Rangpur |  | 121 |  | 1119
|  |  |  | Total |  | 1042 |  | 15058
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:39 | 10:06 | Ishurdi 230/132kV S/S 230/132 kV T-01 HT Tripped showing siemence7sj8041 relays Due to
oil temperature trip
| 08:39 | 10:07 | Ishurdi 230/132kV S/S 230/132 kV T-01 LT Tripped showing siemence7saj8041 relays Due to
oil temperature trip
|  | 10:12 | Khulshi 132/33kV S/S 415T (T2) HT is restored.
| 10:16 | 12:24 | Chowmuhani 230/132/33kV S/S TR3 Forced S/D Due to 33kv Datterhat feeder R phase loop | [7 empty] | 25.0MW load
|  |  | Red-hot. | [7 empty] | interrup.
| 12:00 |  | Day Peak Generation: 12493MW.
| 16:01 | 17:57 | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to 33kV Kobirpur Feeder CB | [7 empty] | 30.0MW load
|  |  | Replacement work | [7 empty] | interrup.
| 16:02 | 17:55 | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to 33kV Kobirpur Feeder CB | [7 empty] | 30.0MW load
|  |  | Replacement work | [7 empty] | interrup.
|  | 19:07 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 is restored.
|  | 19:08 | Halishahar-Khulshi 132kV Ckt-1 is restored.
|  | 19:09 | Halishahar-Khulshi 132kV Ckt-2 is restored.
|  | 19:19 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 is restored.
|  | 19:22 | Khulshi 132/33kV S/S Khulshi-Halishahar CKT-3 is restored.
|  | 21:09 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-2 is restored.
| 21:12 | 21:35 | Feni 132/33kV S/S T-1(405T) LT Tripped showing Siemens SIPROTEC relays. | [7 empty] | 54.0MW load
interrup.
| 06:17 |  | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) LT Forced S/D Due to 33kv DS Hot spot
maintenance.
| 06:18 |  | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) HT Forced S/D Due to 33kv DS Hot spot
maintenance.
| 06:28 |  | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 Project Work S/D Due to Project work by
PGNS (G2G)
| 06:29 |  | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-2 Project Work S/D Due to Project work by
PGNS (G2G)
| 07:18 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to Korapur 33kv feeder B phase finger | [7 empty] | 23.0MW load
|  |  | work | [7 empty] | interrup.
| 07:19 |  | Halishahar-Khulshi 132kV Ckt-1 Scheduled S/D from Halishahar 132/33kV end Due to OPGW
Cable stringing and Fiber splicing
| 07:19 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Hot spot maintenance
| 07:20 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to 33kv korapur feeder B phase finger | [7 empty] | 23.0MW load
|  |  | work | [7 empty] | interrup.
| 07:20 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D
| 07:21 |  | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 Scheduled S/D Due to OPGW cable
stringing and Fiber splicing
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 325 | 7268400 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 120 | 2965411 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 145680 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6996185 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 324720 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 2781120 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 604892 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 469101 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 388200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 445680 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 741600 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 1630909 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 68 | 719424 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1359360 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 986400 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 186025 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 383760 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 315 | 8069091 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3372000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 1960.42 | 39837958
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 102430.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 38070 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1079520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5318487 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 186 | 4414040 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 99 | 1967127 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 23 | 296080 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 395396 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 351360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 34 | 465600 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 43 | 529920 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 13441 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 331200 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 392238 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 106 | 2008109 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 264000 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 92 | 1628400 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 152 | 946764 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1190 | 28652725 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 38 | 522240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 20829090.91 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 3510.36 | 70546238.71
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 0 | 916000 | Under Maintenance
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 356 | 8886000 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 817776 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 44 | 900480 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 180 | 2576000 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1248609 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 570400 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 14 | 395200 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 379317 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 178 | 3610080 | -
| Import (Tripura) |  | Import | 0 | 160 | 164 | 34442560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 678173 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 319080 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 1811460 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 176400 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 88 | 842880 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 232300 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1396 | 58802715
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 123721 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 154 | 2265600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1348800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 298880 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 279120 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 428760 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 251 | 4756781
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 70349 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 963000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 934320 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 146 | 3519000 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 63 | 625920 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2433850 | plant availability zero
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 197808 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7559000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 305 | 6808000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1011 | 23111247
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 901 | 21555636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 27 | 139200 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 37872 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 257040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1161 | 27665460 | AGC+FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2142 | 50567208
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1050 | 16596364 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 356640 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 60 | 1603000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 570 | 12699636.36 | Coal shortage
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5320260 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 435600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 202 | 6523000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1326 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2153 | 43535826.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 280768 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 134931 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 175 | 4223636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 377 | 9033751 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 14 | 112000 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 295541 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 653104 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 100 | 805728 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 57 | 384000 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 23820 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 805.4 | 26067129 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 288064 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 628650 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1708.6 | 42931122
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1093964 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 4030000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 89 | 680476 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47047.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 106 | 1812552 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 230179 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1376640 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 402 | 9270858.44
Eastern Grid Total |  |  |  |  | 17440.562 | 8128.78 | 197054939.71
Western Grid Total |  |  |  |  | 11731.125 | 6405.6 | 146305014.8
National Grid Total |  |  |  |  | 29171.687 | 14534.38 | 343359954.51
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-08-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9628.36 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4443.8 | MW
i) Dhaka area |  |  | 4999.36 |  | MW | i) Khulna area |  |  |  | 1637 | MW
ii) Chattogram area |  |  | 1465 |  | MW | ii) Barishal area |  |  |  | 422.4 | MW
iii) Cumilla area |  |  | 1379 |  | MW | iii) Rajshahi area |  |  |  | 1386.4 | MW
iv) Mymensingh area |  |  | 1161 |  | MW | iv) Rangpur area |  |  |  | 998 | MW
v) Sylhet area |  |  | 624 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14072.16 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 01:00 | 67 | HaripurSBU | 132 | 01:00 | 133 | Narshingdi | 187 | 01:00 | 199 | Uttara | 84 | 19:00
2 | AKSML | 78 | 23:00 | 68 | Hasnabad | 82 | 00:00 | 134 | Natore | 146 | 19:30 | 200 | UttaraNew | 51 | 13:00
3 | Aftabnagar | 40 | 21:00 | 69 | Hathazari | 81 | 20:00 | 135 | Nawabganj | 61.8 | 22:00 | 201 | Zigatola | 86 | 13:00
4 | Agargaon | 101 | 13:00 | 70 | Hatirjheel | 61 | 16:00 | 136 | Netrakona | 116 | 21:00
5 | Agrabad | 54 | 00:00 | 71 | Ishurdi | 76 | 19:30 | 137 | New | 64 | 00:00
6 | Amnura | 31 | 00:00 | 72 | Jaldhaka | 90 | 19:30 | 138 | Niamatpur | 83 | 22:00
7 | Ashuganj | 89 | 19:30 | 73 | Jamalpur | 127 | 21:00 | 139 | Noapara | 38 | 19:00
8 | BSRM | 191 | 23:00 | 74 | Jashore | 145 | 00:00 | 140 | PHP | 8 | 07:00
9 | Bagerhat | 76 | 23:00 | 75 | Jhenaidah | 99 | 19:30 | 141 | Pabna | 98 | 19:30
10 | Bajitpur | 70 | 20:00 | 76 | Joydebpur | 134 | 19:30 | 142 | Palashbari | 122 | 04:00
11 | Bakerganj | 13.6 | 19:30 | 77 | Joypurhat | 58 | 05:00 | 143 | Panchagarh | 68 | 00:00
12 | Bakulia | 83 | 00:00 | 78 | Juldah | 15 | 11:00 | 144 | Patiya | 11 | 02:00
13 | Banani | 48 | 19:00 | 79 | KSRM | 26 | 07:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 4 | 18:30 | 80 | Kabirpur | 206 | 21:00 | 146 | Patuakhali | 57.5 | 22:00
15 | Barapukuria | 68 | 19:30 | 81 | Kachua | 90 | 19:00 | 147 | Payra | 28 | 13:00
16 | Barguna | 20 | 19:30 | 82 | Kaliganj | 39 | 19:30 | 148 | Postogola | 52 | 00:00
17 | Barishal | 89 | 22:00 | 83 | Kallyanpur | 117 | 13:00 | 149 | Pubail | 41 | 00:00
18 | Barishal-230 | 92 | 19:00 | 84 | Kalurghat | 30 | 01:00 | 150 | Purbachal | 26 | 19:00
19 | Baroaulia | 60 | 15:00 | 85 | Kamrangirchar | 66 | 00:00 | 151 | Purbasadipur | 130 | 22:00
20 | Baroirhat | 57 | 22:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 35 | 19:00
21 | Bashundhara | 183 | 12:00 | 87 | Kasba | 38 | 22:00 | 153 | Rahim | 28 | 02:00
22 | BashundharaCement | 5 | 00:00 | 88 | Kazla | 106 | 13:00 | 154 | Rajbari | 83 | 19:30
23 | Beanibazar | 80 | 19:00 | 89 | Keranigonj | 73 | 13:00 | 155 | Rajendrapur | 115 | 22:00
24 | Benapole | 53 | 20:00 | 90 | Khagrachori | 34 | 19:00 | 156 | Rajshahi | 103 | 19:30
25 | Bhaluka | 170 | 19:30 | 91 | Khulna | 52 | 21:00 | 157 | Rajshahi-230 | 94 | 13:00
26 | Bhandaria | 50 | 19:00 | 92 | Khulshi | 155 | 20:00 | 158 | Ramganj | 104 | 19:00
27 | Bhangura | 36 | 19:00 | 93 | Kishoreganj | 128 | 20:00 | 159 | Rampur | 52 | 21:00
28 | Bheramara(GK) | 63 | 19:00 | 94 | Kodda | 244 | 21:00 | 160 | Rangamati | 18 | 19:00
29 | Bhulta | 205 | 22:00 | 95 | Kulaura | 53 | 13:00 | 161 | Rangpur | 124 | 13:00
30 | Bog-Sherpur | 76 | 19:30 | 96 | Kurigram | 80 | 19:30 | 162 | Ruppur | 4.2 | 12:00
31 | Bogura | 182 | 00:00 | 97 | Kushtia | 135 | 23:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 69 | 22:00 | 98 | Laksam | 29 | 22:00 | 164 | Saidpur | 96 | 19:30
33 | Brahmanbaria | 115 | 00:00 | 99 | Lakshmipur | 45 | 23:00 | 165 | Santhia | 36 | 18:30
34 | Cantonment | 110 | 12:00 | 100 | Lalbag | 62 | 02:00 | 166 | Satkhira | 125 | 22:00
35 | Chandina | 21 | 21:00 | 101 | Lalmonirhat | 70 | 19:00 | 167 | Satmasjid | 97 | 13:00
36 | Chandpur | 74 | 22:00 | 102 | MI_Cement | 11.3 | 04:00 | 168 | Savar | 162 | 23:00
37 | Chandraghona | 32 | 19:00 | 103 | Madanganj | 43 | 12:00 | 169 | SevenRings | 15.37 | 03:00
38 | Chapai | 66 | 06:00 | 104 | Madaripur | 103 | 22:00 | 170 | ShahCement | 25 | 16:00
39 | Charfasson | 28 | 21:00 | 105 | Madartek | 77 | 23:00 | 171 | Shahjadpur | 66 | 22:00
40 | Charsaidpur | 39 | 06:00 | 106 | Madunaghat | 54 | 20:00 | 172 | Shahjibazar | 133 | 19:00
41 | Chauddagram | 72 | 23:00 | 107 | Magura | 65 | 19:30 | 173 | Shahmirpur | 52 | 05:00
42 | Chhatak | 41 | 22:00 | 108 | Mahasthangarh | 83 | 19:30 | 174 | Shariatpur | 81 | 21:00
43 | Chowmuhani | 135 | 22:00 | 109 | Maijdee | 34 | 19:00 | 175 | Sherpur | 154 | 22:00
44 | Chuadanga | 104 | 22:00 | 110 | Manikganj | 128 | 19:00 | 176 | Shikalbaha | 30 | 02:00
45 | Coxsbazar | 149 | 21:00 | 111 | Maniknagar | 69 | 13:00 | 177 | Shitalakhya | 58 | 13:00
46 | Cumilla(N) | 126 | 23:00 | 112 | Matarbari | 58 | 20:00 | 178 | Sholosohor | 45 | 22:00
47 | Cumilla(S) | 167 | 22:00 | 113 | Matuail | 64 | 00:00 | 179 | Shomvuganj | 50 | 07:00
48 | Daganbhuiyan | 34 | 20:00 | 114 | Metrorail_Motijheel | 24 | 17:00 | 180 | Shyampur | 150 | 12:00
49 | Daudkandi | 127 | 22:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 105 | 13:00
50 | DhakaUniversity | 44 | 13:00 | 116 | Millgate | 74 | 12:00 | 182 | Sirajganj | 110 | 00:00
51 | Dhamrai | 96 | 00:00 | 117 | Mirpur | 139 | 13:00 | 183 | Sitakunda | 32 | 21:00
52 | Dhanmondi | 87 | 19:00 | 118 | Mirsorai | 50 | 08:00 | 184 | Sonargaon | 132 | 00:00
53 | Dohazari | 103 | 19:30 | 119 | Mirzapur | 41 | 19:00 | 185 | Sreemongol | 82 | 05:00
54 | Faridpur | 165 | 22:00 | 120 | Mithapukur | 84 | 19:30 | 186 | Sreepur | 117 | 22:00
55 | Fatullah | 74 | 01:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 49.2 | 23:00
56 | Fenchuganj | 40 | 15:00 | 122 | Mogbazar | 49.5 | 19:30 | 188 | Sunamganj | 56 | 13:00
57 | Feni | 102 | 23:00 | 123 | Mongla | 38 | 00:00 | 189 | Sylhet | 107 | 20:00
58 | GPH | 2 | 03:00 | 124 | Motijheel | 36 | 13:00 | 190 | Sylhet_(South) | 84 | 21:00
59 | Ghatail | 104 | 19:00 | 125 | Muktagacha | 43 | 15:00 | 191 | TK | 22 | 19:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 106 | 01:00 | 192 | Tangail | 184 | 20:00
61 | Ghorashal-230 | 99 | 02:00 | 127 | Muradnagar | 47 | 19:00 | 193 | Taraganj | 36 | 19:30
62 | Goalpara | 36 | 19:30 | 128 | Mymensingh | 144 | 00:00 | 194 | Tasnim | 40 | 17:00
63 | Gollamari | 94 | 13:00 | 129 | Nabinagar | 88 | 12:00 | 195 | Thakurgaon | 119 | 20:00
64 | Gopalganj | 108 | 19:30 | 130 | Naogaon | 126 | 21:00 | 196 | Tongi | 129 | 23:00
65 | Gulshan | 82 | 19:00 | 131 | Narail | 57 | 19:30 | 197 | Ullahpara | 39 | 19:30
66 | Halishahar | 71.5 | 13:00 | 132 | Narinda | 48 | 13:00 | 198 | Ullon | 42 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13663.82 | 2027 |  | 15781.82
1:00 | 13217.69 | 1887 |  | 15189.69
2:00 | 13085.26 | 1787 |  | 14952.26
3:00 | 12964.78 | 1739 |  | 14781.78
4:00 | 12926.89 | 1667 |  | 14668.89
5:00 | 12661.91 | 1248 |  | 13965.91
6:00 | 12229.1 | 629 |  | 12886.41
7:00 | 12039.41 | 668 |  | 12737.47
8:00 | 11893.95 | 206 |  | 12109.22
9:00 | 11539.62 | 136 |  | 11681.74
10:00 | 11760.28 | 26 |  | 11787.45
11:00 | 11797.21 | 0 |  | 11797.21
12:00 | 12500.51 | 39 |  | 12541.27
13:00 | 13170.03 | 512 |  | 13705.07
14:00 | 12551.98 | 193 |  | 12753.67
15:00 | 12546.4 | 248 |  | 12805.56
16:00 | 12333.63 | 125 |  | 12464.26
17:00 | 11852.72 | 81 |  | 11937.37
18:00 | 11818.24 | 76 |  | 11897.66
19:00 | 13208.7 | 330 |  | 13553.7
19:30 | 14354.01 | 471 |  | 14846.01
20:00 | 14313.85 | 897 |  | 15250.85
21:00 | 14534.38 | 1042 |  | 15623.38
22:00 | 14536.52 | 994 |  | 15575.52
23:00 | 14390.76 | 1484 |  | 15941.76
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 07-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 167 | 41 | 550 | 178 | 1540 | 614 | Ishurdi-Ghorashal Ckt-1 | Export | 3758618.18
1:00 | 142 | 30 | 500 | 152 | 1470 | 566
2:00 | 133 | 23 | 480 | 140 | 1442 | 538 |  | Import | 0
3:00 | 137 | 27 | 480 | 140 | 1450 | 552
4:00 | 135 | 25 | 460 | 122 | 1438 | 530 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 134 | 21 | 470 | 124 | 1440 | 536
6:00 | 108 | 19 | 330 | 100 | 1254 | 492 |  | Import | 0
7:00 | 187 | 73 | 0 | 0 | 1066 | 480
8:00 | 186 | 72 | 0 | 0 | 1528 | 600 | Sirajganj-Sreepur Ckt-1 | Export | 1207000
9:00 | 169 | 54 | 0 | 0 | 2000 | 634
10:00 | 156 | 39 | 0 | 0 | 2132 | 690 |  | Import | 0
11:00 | 167 | 51 | 0 | 0 | 2208 | 764
12:00 | 171 | 53 | 0 | 0 | 2116 | 746 | Sirajganj-Sreepur Ckt-2 | Export | 1000000
13:00 | 158 | 44 | 0 | 0 | 1884 | 634
14:00 | 156 | 39 | 0 | 0 | 1850 | 646 |  | Import | 0
15:00 | 167 | 46 | 0 | 0 | 1930 | 504
16:00 | 143 | 28 | 0 | 0 | 1900 | 638 | Gopalganj-Aminbazar Ckt-1 | Export | 19380000
17:00 | 164 | 48 | 0 | 0 | 1824 | 648
18:00 | 149 | 33 | 0 | 0 | 1702 | 594 |  | Import | 0
18:30 | 153 | 35 | 0 | 0 | 1568 | 604
19:00 | 184 | 78 | 0 | 0 | 1246 | 550 | Gopalganj-Aminbazar Ckt-2 | Export | 19420000
19:30 | 159 | 41 | 190 | 140 | 1122 | 494
20:00 | 164 | 39 | 250 | 162 | 1288 | 542 |  | Import | 0
21:00 | 179 | 67 | 250 | 157 | 1276 | 540
22:00 | 179 | 65 | 290 | 172 | 1218 | 508 |  | Total Export | 44765618.18
23:00 | 186 | 79 | 336 | 170 | 1288 | 504 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7097.62 | 6566.2 | 13663.82 | DAILY GENERATION CURVE
00:30 | 7022.91 | 6417.845 | 13440.755
01:00 | 6948.2 | 6269.49 | 13217.69 | 07-08-2026
01:30 | 6887.7 | 6263.775 | 13151.475
02:00 | 6827.2 | 6258.06 | 13085.26
02:30 | 6761.7 | 6263.32 | 13025.02
03:00 | 6696.2 | 6268.58 | 12964.78
03:30 | 6680.6 | 6265.235 | 12945.835
04:00 | 6665 | 6261.89 | 12926.89
04:30 | 6575.5 | 6218.9 | 12794.4
05:00 | 6486 | 6175.91 | 12661.91
05:30 | 6499.215 | 5946.29 | 12445.505
06:00 | 6512.43 | 5716.67 | 12229.1
06:30 | 6548.51 | 5585.745 | 12134.255
07:00 | 6584.59 | 5454.82 | 12039.41
07:30 | 6450.7 | 5515.98 | 11966.68
08:00 | 6316.81 | 5577.14 | 11893.95
08:30 | 6044.59 | 5672.195 | 11716.785
09:00 | 5772.37 | 5767.25 | 11539.62
09:30 | 5796.125 | 5853.825 | 11649.95
10:00 | 5819.88 | 5940.4 | 11760.28
10:30 | 5859.98 | 5918.765 | 11778.745
11:00 | 5900.08 | 5897.13 | 11797.21
11:30 | 6136.1 | 6012.76 | 12148.86
12:00 | 6372.12 | 6128.39 | 12500.51
12:30 | 6621.935 | 6213.335 | 12835.27
13:00 | 6871.75 | 6298.28 | 13170.03
13:30 | 6736.835 | 6124.17 | 12861.005
14:00 | 6601.92 | 5950.06 | 12551.98
14:30 | 6622.83 | 5926.36 | 12549.19
15:00 | 6643.74 | 5902.66 | 12546.4
15:30 | 6593.24 | 5846.775 | 12440.015
16:00 | 6542.74 | 5790.89 | 12333.63
16:30 | 6435.875 | 5657.3 | 12093.175
17:00 | 6329.01 | 5523.71 | 11852.72
17:30 | 6387.535 | 5447.945 | 11835.48
18:00 | 6446.06 | 5372.18 | 11818.24
18:30 | 6940.42 | 5573.05 | 12513.47
19:00 | 7434.78 | 5773.92 | 13208.7
19:30 | 8123.78 | 6230.23 | 14354.01
20:00 | 8126.78 | 6187.07 | 14313.85
20:30 | 8127.78 | 6296.335 | 14424.115 |  | Executive Engineer
21:00 | 8128.78 | 6405.6 | 14534.38 |  | Network Operation Division
21:30 | 8129.88 | 6405.57 | 14535.45
22:00 | 8130.98 | 6405.54 | 14536.52
22:30 | 8070.8 | 6392.84 | 14463.64
23:00 | 8010.62 | 6380.14 | 14390.76

## En-Curve
QF-LDC-12
Date | 07-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2467 | 1272 | 875 | 38 | 154 | 1421 | 221 | 5007 | 0 | 594.42 | 1609.4 | 0 | 0 | 5 | 2027 | DAILY ENERGY CURVE
00:30 | 2465 | 1279 | 874.5 | 38 | 154 | 1425.745 | 221.5 | 4942.5 | 0 | 522.21 | 1510.8 | 0 | 0 | 7.5 | 1957 | 07-08-2026
01:00 | 2463 | 1286 | 874 | 38 | 154 | 1430.49 | 222 | 4878 | 0 | 450 | 1412.2 | 0 | 0 | 10 | 1887
01:30 | 2448.5 | 1306.5 | 874 | 38 | 152 | 1431.775 | 221 | 4870 | 0 | 414 | 1382.2 | 0 | 0 | 13.5 | 1837 | Energy Generated | 343.36 |  | MKWHr
02:00 | 2434 | 1327 | 874 | 38 | 150 | 1433.06 | 220 | 4862 | 0 | 378 | 1352.2 | 0 | 0 | 17 | 1787 | Energy not Served | 18.041 |  | MKWHr
02:30 | 2430.5 | 1334 | 874.5 | 38 | 150 | 1436.32 | 220 | 4861 | 0 | 374.5 | 1286.7 | 0 | 0 | 19.5 | 1763 | Total Energy Requirement | 361.401 |  | MKWHr
03:00 | 2427 | 1341 | 875 | 38 | 150 | 1439.58 | 220 | 4860 | 0 | 371 | 1221.2 | 0 | 0 | 22 | 1739
03:30 | 2420.5 | 1340.5 | 875 | 38 | 148 | 1447.235 | 220 | 4857 | 0 | 364.5 | 1211.6 | 0 | 0 | 23.5 | 1703
04:00 | 2414 | 1340 | 875 | 38 | 146 | 1454.89 | 220 | 4854 | 0 | 358 | 1202 | 0 | 0 | 25 | 1667
04:30 | 2295.5 | 1362.5 | 875 | 38 | 146 | 1453.9 | 220 | 4853 | 0 | 350 | 1180 | 0 | 0 | 20.5 | 1457.5
05:00 | 2177 | 1385 | 875 | 38 | 146 | 1452.91 | 220 | 4852 | 0 | 342 | 1158 | 0 | 0 | 16 | 1248
05:30 | 2144 | 1408 | 875 | 38 | 139 | 1302.37 | 220 | 4845.5 | 7.635 | 342 | 1107 | 0 | 0 | 17 | 938.5
06:00 | 2111 | 1431 | 875 | 38 | 132 | 1151.83 | 220 | 4839 | 15.27 | 342 | 1056 | 0 | 0 | 18 | 629
06:30 | 2071.5 | 1459.5 | 874.5 | 38 | 131 | 1077.985 | 220.5 | 4787 | 48.27 | 350.5 | 1057.5 | 0 | 0 | 18 | 648.5
07:00 | 2032 | 1488 | 874 | 38 | 130 | 1004.14 | 221 | 4735 | 81.27 | 359 | 1059 | 0 | 0 | 18 | 668
07:30 | 2089.5 | 1449 | 874.5 | 38 | 129 | 1052.84 | 220.5 | 4698 | 121.13 | 349.21 | 929.5 | 0 | 0 | 15.5 | 437
08:00 | 2147 | 1410 | 875 | 38 | 128 | 1101.54 | 220 | 4661 | 160.99 | 339.42 | 800 | 0 | 0 | 13 | 206
08:30 | 2155 | 1426 | 887.5 | 38 | 127 | 1125.41 | 221 | 4626.5 | 238.955 | 344.92 | 513 | 0 | 0 | 13.5 | 171
09:00 | 2163 | 1442 | 900 | 38 | 126 | 1149.28 | 222 | 4592 | 316.92 | 350.42 | 226 | 0 | 0 | 14 | 136
09:30 | 2156.5 | 1414.5 | 901 | 38 | 131 | 1178.71 | 222 | 4597 | 376.32 | 361.92 | 254.5 | 0 | 0 | 18.5 | 81
10:00 | 2150 | 1387 | 902 | 38 | 136 | 1208.14 | 222 | 4602 | 435.72 | 373.42 | 283 | 0 | 0 | 23 | 26
10:30 | 2168.5 | 1396 | 901.5 | 38 | 139 | 1204.64 | 222 | 4626.5 | 428.185 | 363.92 | 270 | 0 | 0 | 20.5 | 13
11:00 | 2187 | 1405 | 901 | 38 | 142 | 1201.14 | 222 | 4651 | 420.65 | 354.42 | 257 | 0 | 0 | 18 | 0
11:30 | 2144.5 | 1384 | 901 | 38 | 145 | 1203.65 | 222 | 4676 | 501.29 | 359.92 | 557.5 | 0 | 0 | 16 | 19.5
12:00 | 2102 | 1363 | 901 | 38 | 148 | 1206.16 | 222 | 4701 | 581.93 | 365.42 | 858 | 0 | 0 | 14 | 39
12:30 | 2125.5 | 1375.5 | 901 | 38 | 151 | 1210.45 | 222 | 4693.5 | 594.9 | 389.42 | 1120 | 0 | 0 | 14 | 275.5
13:00 | 2149 | 1388 | 901 | 38 | 154 | 1214.74 | 222 | 4686 | 607.87 | 413.42 | 1382 | 0 | 0 | 14 | 512
13:30 | 2144.5 | 1393.5 | 900.5 | 38 | 150 | 1121.83 | 222 | 4593.5 | 585.755 | 362.92 | 1334 | 0 | 0 | 14.5 | 352.5
14:00 | 2140 | 1399 | 900 | 38 | 146 | 1028.92 | 222 | 4501 | 563.64 | 312.42 | 1286 | 0 | 0 | 15 | 193
14:30 | 2144 | 1407.5 | 900.5 | 38 | 145 | 979.445 | 222 | 4600 | 496.325 | 311.92 | 1287 | 0 | 0 | 17.5 | 220.5
15:00 | 2148 | 1416 | 901 | 38 | 144 | 929.97 | 222 | 4699 | 429.01 | 311.42 | 1288 | 0 | 0 | 20 | 248
15:30 | 2131 | 1405 | 901 | 38 | 139 | 919.005 | 222 | 4708 | 353.59 | 310.92 | 1291 | 0 | 0 | 21.5 | 186.5
16:00 | 2114 | 1394 | 901 | 38 | 134 | 908.04 | 222 | 4717 | 278.17 | 310.42 | 1294 | 0 | 0 | 23 | 125
16:30 | 2166 | 1381 | 901 | 38 | 133 | 867.89 | 222 | 4737 | 213.365 | 294.42 | 1113.5 | 0 | 0 | 26 | 103
17:00 | 2218 | 1368 | 901 | 38 | 132 | 827.74 | 222 | 4757 | 148.56 | 278.42 | 933 | 0 | 0 | 29 | 81
17:30 | 2219 | 1413.5 | 901 | 38 | 129 | 817.625 | 222 | 4721.5 | 92.435 | 283.42 | 963.5 | 0 | 0 | 34.5 | 78.5
18:00 | 2220 | 1459 | 901 | 38 | 126 | 807.51 | 222 | 4686 | 36.31 | 288.42 | 994 | 0 | 0 | 40 | 76
18:30 | 2265 | 1490.5 | 901 | 38 | 141 | 794.215 | 221.5 | 4869 | 18.155 | 439.42 | 1296.18 | 0 | 0 | 39.5 | 203
19:00 | 2310 | 1522 | 901 | 38 | 156 | 780.92 | 221 | 5052 | 0 | 590.42 | 1598.36 | 0 | 0 | 39 | 330
19:30 | 2313 | 1577 | 901 | 38 | 162 | 786.23 | 220 | 5448 | 0 | 695.42 | 2186.36 | 0 | 0 | 27 | 471
20:00 | 2254 | 1515 | 892 | 38 | 152 | 774.07 | 220 | 5501 | 0 | 706.42 | 2215.36 | 0 | 0 | 46 | 897
20:30 | 2285 | 1527 | 896.5 | 38 | 158 | 789.735 | 220 | 5503 | 0 | 709.42 | 2255.46 | 0 | 0 | 42 | 969.5
21:00 | 2316 | 1539 | 901 | 38 | 164 | 805.4 | 220 | 5505 | 0 | 712.42 | 2295.56 | 0 | 0 | 38 | 1042
21:30 | 2330 | 1528.5 | 901 | 38 | 166 | 809.37 | 220 | 5502 | 0 | 705.42 | 2301.16 | 0 | 0 | 34 | 1018
22:00 | 2344 | 1518 | 901 | 38 | 168 | 813.34 | 220 | 5499 | 0 | 698.42 | 2306.76 | 0 | 0 | 30 | 994
22:30 | 2333.5 | 1528 | 901 | 38 | 163 | 802.14 | 220 | 5506 | 0 | 698.92 | 2248.08 | 0 | 0 | 25 | 1239
23:00 | 2323 | 1538 | 901 | 38 | 158 | 790.94 | 220 | 5513 | 0 | 699.42 | 2189.4 | 0 | 0 | 20 | 1484
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 07:00 | 364 | 12:00 | Madunaghat | 405 | 06:00 | 393 | 11:00
Amtali | 414 | 05:00 | 409 | 22:00 | Meghnaghat | 387 | 07:00 | 363 | 11:00
Ashuganj | 372 | 07:00 | 357 | 11:00 | Mirsorai | 403 | 06:00 | 387 | 11:00
Bhulta | 399 | 07:00 | 373 | 11:00 | Payra | 416 | 07:00 | 410 | 23:00
Bibiana | 383 | 07:00 | 372 | 12:00 | Rahanpur | 413 | 23:00 | 396 | 04:00
BIPTC | 402 | 04:00 | 393 | 20:00 | Rampal | 399 | 08:00 | 389 | 12:00
Bogura | 397 | 21:00 | 377 | 04:00
Gopalganj | 396 | 07:00 | 386 | 00:00
Kaliakoir | 372 | 07:00 | 357 | 11:00
Korerhat | 403 | 06:00 | 387 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 07:00 | 223 | 12:00 | Ishurdi | 237 | 20:00 | 225 | 19:00
AKSML | 237 | 06:00 | 221 | 10:00 | Jhenaidah | 228 | 11:00 | 215 | 19:00
Aminbazar | 235 | 07:00 | 222 | 12:00 | Kachua | 232 | 06:00 | 219 | 11:00
Ashuganj | 228 | 07:00 | 208 | 11:00 | Kaliakoir | 233 | 07:00 | 223 | 11:00
Ashuganj-400 | 228 | 07:00 | 208 | 11:00 | Keranigonj | 231 | 07:00 | 220 | 12:00
Baghabari | 237 | 18:00 | 229 | 00:00 | Khulna(S) | 228 | 08:00 | 221 | 22:00
Barapukuria | 227 | 18:30 | 218 | 05:00 | Korerhat | 231 | 07:00 | 220 | 11:00
Barapukuria-230 | 227 | 18:30 | 218 | 05:00 | Madunaghat | 240 | 02:00 | 233 | 11:00
Barishal | 229 | 07:00 | 223 | 22:00 | Madunaghat-400 | 242 | 05:00 | 230 | 23:00
Bheramara | 234 | 00:00 | 222 | 19:00 | Maniknagar | 226 | 06:00 | 217 | 11:00
Bhulta | 230 | 07:00 | 216 | 11:00 | Meghnaghat | 235 | 06:00 | 224 | 12:00
Bibiana | 222 | 07:00 | 213 | 12:00 | Meghnaghat-400 | 232 | 07:00 | 221 | 11:00
BIPTC | 237 | 00:00 | 23 | 03:00 | Mirsorai | 234 | 06:00 | 224 | 11:00
Bogura | 247 | 18:30 | 235 | 05:00 | Naogaon | 230 | 18:30 | 216 | 05:00
Bogura-400 | 247 | 18:30 | 235 | 05:00 | Purbasadipur | 225 | 15:00 | 216 | 05:00
Borhanuddin | 231 | 07:00 | 227 | 13:00 | Rajshahi | 234 | 00:00 | 223 | 13:00
BSRM | 231 | 06:00 | 220 | 11:00 | Rampal | 229 | 11:00 | 220 | 13:00
Charfasson | 232 | 16:00 | 22 | 20:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 231 | 07:00 | 222 | 10:00 | Rampura | 229 | 07:00 | 216 | 11:00
Cumilla(N) | 228 | 07:00 | 214 | 11:00 | Shikalbaha | 239 | 00:00 | 232 | 11:00
Faridpur | 225 | 07:00 | 219 | 12:00 | Shyampur | 231 | 07:00 | 220 | 11:00
Fenchuganj | 221 | 19:30 | 215 | 13:00 | Siddhirganj | 229 | 04:00 | 218 | 11:00
Feni | 229 | 07:00 | 217 | 11:00 | Sirajgonj | 238 | 07:00 | 233 | 02:00
Ghorashal | 230 | 03:00 | 215 | 12:00 | Sreepur | 230 | 19:00 | 198 | 11:00
Ghorashal-230 | 219 | 06:00 | 193 | 19:00 | Tongi | 225 | 04:00 | 215 | 00:00
Gopalganj | 225 | 06:00 | 220 | 12:00
GPH | 237 | 06:00 | 227 | 07:00
Haripur | 229 | 07:00 | 218 | 11:00
Hasnabad | 230 | 06:00 | 28 | 19:00
Hathazari | 238 | 02:00 | 231 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 05:00 | 132 | 13:00 | Madartek | 139 | 04:00 | 130 | 11:00
Agargaon | 141 | 06:00 | 134 | 12:00 | Madunaghat | 139 | 05:00 | 134 | 11:00
Agrabad | 137 | 01:00 | 132 | 12:00 | Magura | 135 | 10:00 | 127 | 13:00
AKS | 135 | 01:00 | 131 | 08:00 | Mahasthangarh | 138 | 16:00 | 130 | 04:00
Aminbazar | 134 | 07:00 | 127 | 11:00 | Maijdee | 129 | 02:00 | 122 | 11:00
Amnura | 138 | 00:00 | 129 | 13:00 | Manikganj | 131 | 19:00 | 125 | 15:00
Ashuganj | 131 | 07:00 | 119 | 11:00 | Maniknagar | 142 | 07:00 | 134 | 12:00
Ashuganj-230 | 132 | 06:00 | 123 | 11:00 | Matarbari | 130 | 14:00 | 119 | 12:00
Bagerhat | 131 | 08:00 | 124 | 23:00 | Matuail | 137 | 07:00 | 130.6 | 12:00
Bajitpur | 125 | 05:00 | 116 | 11:00 | Metrorail_Motijheel | 142 | 07:00 | 134 | 12:00
Bakerganj | 135 | 07:00 | 129 | 22:00 | Metrorail_Uttara | 1330 | 09:00 | 129 | 11:00
Bakulia | 137 | 14:00 | 132 | 11:00 | Millgate | 137 | 18:00 | 130 | 11:00
Banani | 139 | 04:00 | 130 | 12:00 | Mirpur | 133 | 07:00 | 125 | 11:00
Bangabhaban | 140 | 05:00 | 134 | 12:00 | Mirzapur | 132 | 09:00 | 127 | 00:00
Barapukuria | 138 | 15:00 | 128 | 05:00 | Mithapukur | 135 | 20:00 | 126 | 05:00
Barguna | 134 | 07:00 | 129 | 22:00 | MI_Cement | 137.4 | 07:00 | 130 | 12:00
Barishal | 134 | 18:00 | 129 | 22:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal-230 | 134 | 07:00 | 129 | 22:00 | Mogbazar | 141 | 07:00 | 132 | 12:00
Baroaulia | 138 | 07:00 | 132 | 11:00 | Mongla | 130 | 10:00 | 124 | 23:00
Baroirhat | 133 | 07:00 | 129 | 10:00 | Motijheel | 140 | 05:00 | 134 | 12:00
Bashundhara | 140 | 07:00 | 129 | 12:00 | Muktagacha | 128 | 09:00 | 12 | 21:00
BashundharaCement | 135 | 01:00 | 130 | 12:00 | Munshiganj | 135 | 07:00 | 128 | 11:00
Beanibazar | 123 | 07:00 | 116 | 13:00 | Muradnagar | 130 | 06:00 | 122 | 11:00
Benapole | 132 | 10:00 | 118 | 00:00 | Mymensingh | 128 | 14:00 | 107 | 11:00
Bhaluka | 130 | 07:00 | 117 | 09:00 | Nabinagar | 134 | 07:00 | 127 | 12:00
Bhandaria | 130 | 05:00 | 125 | 23:00 | Naogaon | 138 | 16:00 | 130 | 05:00
Bhangura | 136 | 15:00 | 129 | 00:00 | Narail | 135 | 10:00 | 126 | 19:00
Bheramara | 137 | 00:00 | 131 | 19:00 | Narinda | 142 | 07:00 | 134 | 12:00
Bheramara(GK) | 138 | 00:00 | 132 | 13:00 | Narshingdi | 130 | 06:00 | 116 | 23:00
Bhulta | 131 | 07:00 | 124 | 12:00 | Natore | 136 | 00:00 | 131 | 05:00
Bhulta-400 | 133 | 07:00 | 125 | 11:00 | Nawabganj | 140 | 07:00 | 133 | 11:00
Bog-Sherpur | 139 | 18:30 | 132 | 05:00 | Netrakona | 121 | 19:00 | 106 | 11:00
Bogura | 141 | 18:30 | 134 | 02:00 | New | 139 | 07:00 | 131 | 11:00
Bogura-230 | 142 | 18:30 | 134 | 05:00 | Niamatpur | 136 | 18:00 | 130 | 04:00
Brahmanbaria | 127 | 07:00 | 115 | 11:00 | Noapara | 135 | 10:00 | 129 | 22:00
Cantonment | 141 | 07:00 | 134 | 11:00 | Pabna | 136 | 10:00 | 131 | 13:00
Chandina | 133 | 07:00 | 125 | 11:00 | Palashbari | 133 | 15:00 | 124 | 05:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandpur | 135 | 07:00 | 121 | 11:00 | Panchagarh | 137 | 13:00 | 127 | 11:00
Chandraghona | 139 | 05:00 | 136 | 09:00 | Patiya | 137 | 19:00 | 132 | 09:00
Chapai | 135 | 23:00 | 128 | 03:00 | Patnitala | 133 | 13:00 | 127 | 05:00
Charsaidpur | 137 | 07:00 | 129 | 12:00 | Patuakhali | 135 | 06:00 | 130 | 11:00
Chauddagram | 132 | 06:00 | 125 | 11:00 | Payra | 136 | 08:00 | 134 | 21:00
Chhatak | 121 | 07:00 | 114 | 13:00 | PHP | 133 | 02:00 | 127 | 11:00
Chowmuhani | 130 | 07:00 | 125 | 10:00 | Postogola | 138 | 06:00 | 131 | 12:00
Chuadanga | 135 | 09:00 | 125 | 23:00 | Pubail | 133 | 10:00 | 117 | 23:00
Coxsbazar | 129 | 14:00 | 119 | 19:30 | Purbachal | 139 | 02:00 | 131 | 11:00
Cumilla(N) | 133 | 07:00 | 125 | 11:00 | Purbasadipur | 136 | 19:00 | 130 | 06:00
Cumilla(S) | 133 | 07:00 | 123 | 19:30 | Rahanpur | 138 | 18:30 | 133 | 01:00
Daganbhuiyan | 133 | 07:00 | 125 | 11:00 | Rahanpur-400 | 138 | 18:30 | 133 | 01:00
Daudkandi | 130 | 07:00 | 122 | 11:00 | Rahim | 137 | 07:00 | 124 | 03:00
DhakaUniversity | 140 | 07:00 | 131 | 11:00 | Rajbari | 128 | 07:00 | 117 | 09:00
Dhamrai | 136 | 07:00 | 128 | 00:00 | Rajendrapur | 131 | 22:00 | 113 | 09:00
Dhanmondi | 139 | 07:00 | 131 | 12:00 | Rajshahi | 134 | 00:00 | 127 | 19:00
Dohazari | 134 | 14:00 | 124 | 03:00 | Rajshahi-230 | 135 | 00:00 | 128 | 13:00
Faridpur | 130 | 07:00 | 125 | 22:00 | Ramganj | 131 | 07:00 | 119 | 11:00
Fatullah | 139 | 07:00 | 130 | 12:00 | Rampur | 137 | 04:00 | 132 | 11:00
Fenchuganj | 129 | 04:00 | 126 | 11:00 | Rampura | 139 | 04:00 | 131 | 11:00
Feni | 133 | 03:00 | 125 | 11:00 | Rangamati | 138 | 05:00 | 134 | 11:00
Feni-230 | 134 | 07:00 | 126 | 11:00 | Rangpur | 133 | 16:00 | 28 | 09:00
Ghatail | 126 | 09:00 | 118 | 22:00 | Ruppur | 139 | 20:00 | 132 | 19:00
Ghorashal | 131 | 10:00 | 118 | 23:00 | Saidpur | 135 | 19:00 | 127 | 05:00
Goalpara | 137 | 08:00 | 132 | 13:00 | Santhia | 137 | 07:00 | 131 | 18:30
Gollamari | 136 | 05:00 | 131 | 22:00 | Satkhira | 133 | 05:00 | 125 | 22:00
Gopalganj | 131 | 07:00 | 128 | 13:00 | Satmasjid | 141 | 07:00 | 134 | 12:00
Gopalganj-400 | 133 | 07:00 | 130 | 12:00 | Savar | 134 | 19:30 | 124 | 11:00
Gulshan | 139 | 07:00 | 130 | 12:00 | SevenRings | 136 | 07:00 | 116 | 19:00
Halishahar | 140 | 06:00 | 133 | 11:00 | ShahCement | 137 | 07:00 | 129 | 12:00
Haripur | 137 | 07:00 | 131 | 11:00 | Shahjadpur | 138 | 10:00 | 135 | 12:00
HaripurSBU | 137 | 07:00 | 130 | 11:00 | Shahjibazar | 125 | 19:30 | 116 | 11:00
Hasnabad | 137 | 05:00 | 133 | 12:00 | Shahmirpur | 139 | 14:00 | 132 | 07:00
Hathazari | 139 | 02:00 | 135 | 10:00 | Shariatpur | 132 | 07:00 | 128 | 12:00
Hatirjheel | 140 | 07:00 | 131 | 11:00 | Sherpur | 127 | 19:00 | 110 | 01:00
Ishurdi | 139 | 00:00 | 133 | 19:00 | Shikalbaha | 128 | 06:00 | 122 | 10:00
Jaldhaka | 132 | 15:00 | 125 | 05:00 | Shikalbaha-230 | 139 | 07:00 | 135 | 09:00
Jamalpur | 130 | 09:00 | 116 | 01:00 | Shitalakhya | 137.3 | 07:00 | 130 | 12:00
Jashore | 133 | 09:00 | 124 | 13:00 | Sholosohor | 138 | 06:00 | 132 | 11:00
Jhenaidah | 138 | 09:00 | 125 | 22:00 | Shomvuganj | 124 | 07:00 | 110 | 11:00
Jhenaidah-230 | 138 | 07:00 | 129 | 19:00 | Shyampur | 138 | 07:00 | 130 | 12:00
Joydebpur | 135 | 19:00 | 123 | 01:00 | Shyampur-230 | 138 | 06:00 | 131 | 12:00
Joypurhat | 136 | 18:30 | 128 | 03:00 | Siddhirganj | 137 | 06:00 | 130 | 11:00
Juldah | 138 | 05:00 | 133 | 10:00 | Sirajganj | 136 | 09:00 | 129 | 03:00
Kabirpur | 136 | 07:00 | 127 | 11:00 | Sitakunda | 136 | 00:00 | 132 | 01:00
Kachua | 133 | 07:00 | 123 | 11:00 | Sonargaon | 134 | 07:00 | 128 | 11:00
Kaliakoir | 139 | 07:00 | 132 | 11:00 | Sreemongol | 125 | 19:30 | 118 | 11:00
Kaliganj | 136 | 07:00 | 126 | 22:00 | Sreepur | 134 | 22:00 | 117 | 10:00
Kallyanpur | 134 | 19:00 | 126 | 11:00 | Srinagar | 140 | 07:00 | 133 | 11:00
Kalurghat | 138 | 01:00 | 134 | 10:00 | SSM | 140 | 05:00 | 138 | 00:00
Kamrangirchar | 139 | 06:00 | 124 | 11:00 | Sunamganj | 120 | 19:00 | 112 | 13:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 123 | 03:00 | 120 | 11:00
Kasba | 130 | 07:00 | 122 | 11:00 | Sylhet_(South) | 124 | 06:00 | 119 | 13:00
Kazla | 140 | 05:00 | 133 | 13:00 | Tangail | 129 | 09:00 | 121 | 22:00
Keranigonj | 141 | 07:00 | 133 | 12:00 | Taraganj | 133 | 15:00 | 126 | 05:00
Khagrachori | 136 | 02:00 | 132 | 10:00 | Tasnim | 134 | 07:00 | 128 | 11:00
Khulna | 136 | 09:00 | 130 | 22:00 | Thakurgaon | 137 | 13:00 | 127 | 09:00
Khulna(S) | 137 | 08:00 | 132 | 22:00 | TK | 137 | 16:00 | 134 | 02:00
Khulshi | 136 | 00:00 | 130 | 11:00 | Tongi | 138 | 04:00 | 132 | 00:00
Kishoreganj | 126 | 07:00 | 113 | 11:00 | Ullahpara | 136 | 09:00 | 131 | 22:00
Kodda | 136 | 09:00 | 126 | 01:00 | Ullon | 140 | 07:00 | 130 | 12:00
Korerhat | 136 | 06:00 | 130 | 11:00 | Uttara | 137 | 18:00 | 129 | 11:00
KSRM | 137 | 01:00 | 132 | 10:00 | UttaraNew | 137 | 07:00 | 129 | 11:00
Kulaura | 130 | 07:00 | 124 | 13:00 | Zigatola | 142 | 07:00 | 133 | 12:00
Kurigram | 131 | 20:00 | 122 | 04:00
Kushtia | 134 | 02:00 | 126 | 22:00
Laksam | 132 | 07:00 | 123 | 11:00
Lakshmipur | 130 | 07:00 | 122 | 11:00
Lalbag | 139 | 19:00 | 133 | 12:00
Lalmonirhat | 130 | 16:00 | 121 | 06:00
Madanganj | 135 | 01:00 | 130 | 12:00
Madaripur | 133 | 07:00 | 130 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-08-2026 | [28 empty] | Date: | 07-08-2026 | [28 empty] | Date: | 07-08-2026 | [28 empty] | Date: | 07-08-2026 | [28 empty] | Date: | 07-08-2026 | [18 empty] | Date: | 07-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 38 | 16 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 0 | 35 | 52 | 145 | 97 | 0 | 0 | 54 | 0 | 0 | 120 | 295 | 0 | 0 | 293 | 0 | 0 | 0 | 143.42 | 16 | 21 | 0 | 0 | 96 | 16 | 61 | 0 | 5 | 51 | 23 | 17 | 12 | 12 | 0 | 221 | 106 | 20 | 930 | 16 | 0 | 50 | 8 | 101 | 187 | 0 | 0 | 0 | 1224 | 0 | 13 | 8 | 0 | 359 | 0 | 51 | 15 | 182 | 40 | 43 | 0 | 183 | 3 | 13 | 102 | 154 | 52.2 | 0 | 23 | 315 | 0 | 292 | 40 | 39 | 148 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 49 | 0 | 47 | 0 | 0 | 0 | 12 | 7097.62 | 875 | 0 | 0 | 20 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 1421 | 0 | 0 | 0 | 37 | 90 | 0 | 100 | 21 | 52.2 | 0 | 0 | 14 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 163 | 48 | 109 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 600 | 570 | 17 | 6566.2 | 13663.82 | 102
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 17 | 20 | 145 | 147 | 6 | 35 | 54 | 0 | 0 | 120 | 310 | 0 | 0 | 298 | 0 | 0 | 0 | 123 | 16 | 21 | 0 | 0 | 99 | 16 | 30 | 0 | 10 | 51 | 23 | 0 | 12 | 12 | 0 | 222 | 105 | 22 | 810 | 18 | 0 | 46 | 0 | 103 | 187 | 0 | 0 | 0 | 1224 | 0 | 13 | 8 | 0 | 360 | 0 | 51 | 15 | 193 | 37 | 34 | 0 | 186 | 0 | 13 | 97 | 154 | 52.2 | 0 | 23 | 310 | 0 | 292 | 42 | 39 | 150 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 49 | 0 | 47 | 0 | 0 | 0 | 12 | 6948.2 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 1430.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 0 | 14 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 162 | 48 | 110 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 600 | 565 | 17 | 6269.49 | 13217.69 | 101.98
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 17 | 17 | 145 | 147 | 15 | 35 | 0 | 0 | 0 | 120 | 335 | 0 | 0 | 300 | 0 | 0 | 0 | 123 | 16 | 21 | 0 | 0 | 100 | 16 | 16 | 0 | 17 | 0 | 23 | 0 | 12 | 12 | 0 | 220 | 99 | 28 | 785 | 16 | 0 | 46 | 0 | 104 | 187 | 0 | 0 | 0 | 1224 | 0 | 13 | 8 | 0 | 359 | 0 | 51 | 15 | 198 | 37 | 34 | 0 | 186 | 0 | 13 | 106 | 150 | 52.2 | 0 | 23 | 315 | 0 | 293 | 42 | 39 | 155 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 49 | 0 | 47 | 0 | 0 | 0 | 12 | 6827.2 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 1433.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 14 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 163 | 48 | 109 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 600 | 575 | 17 | 6258.06 | 13085.26 | 102
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 17 | 17 | 145 | 48 | 15 | 35 | 0 | 0 | 0 | 120 | 345 | 0 | 0 | 301 | 0 | 0 | 0 | 123 | 16 | 21 | 0 | 0 | 99 | 16 | 18 | 0 | 22 | 0 | 23 | 0 | 12 | 12 | 0 | 220 | 93 | 32 | 780 | 18 | 0 | 49 | 0 | 105 | 187 | 0 | 0 | 0 | 1224 | 0 | 13 | 8 | 0 | 359 | 0 | 51 | 15 | 197 | 37 | 0 | 0 | 187 | 0 | 13 | 104 | 150 | 52.2 | 0 | 16 | 315 | 0 | 293 | 42 | 39 | 155 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 49 | 0 | 47 | 0 | 0 | 0 | 12 | 6696.2 | 875 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 1439.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 14 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 165 | 48 | 111 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 600 | 574 | 17 | 6268.58 | 12964.78 | 102.02
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 17 | 17 | 146 | 48 | 15 | 35 | 0 | 0 | 0 | 120 | 340 | 0 | 0 | 294 | 0 | 0 | 0 | 123 | 16 | 21 | 0 | 0 | 99 | 16 | 18 | 0 | 25 | 0 | 23 | 0 | 12 | 12 | 0 | 220 | 92 | 36 | 780 | 16 | 0 | 50 | 0 | 101 | 187 | 0 | 0 | 0 | 1224 | 0 | 13 | 8 | 0 | 359 | 0 | 51 | 15 | 191 | 37 | 0 | 0 | 183 | 0 | 13 | 105 | 146 | 43 | 0 | 16 | 315 | 0 | 293 | 42 | 39 | 155 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6665 | 875 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 1454.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 160 | 48 | 109 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 600 | 575 | 17 | 6261.89 | 12926.89 | 102.04
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 17 | 17 | 130 | 48 | 15 | 35 | 0 | 0 | 0 | 120 | 360 | 0 | 0 | 300 | 0 | 0 | 0 | 123 | 16 | 21 | 0 | 0 | 96 | 16 | 18 | 0 | 16 | 0 | 23 | 0 | 12 | 12 | 0 | 220 | 91 | 36 | 780 | 17 | 0 | 50 | 0 | 100 | 187 | 0 | 0 | 0 | 1224 | 0 | 12 | 33 | 0 | 359 | 0 | 51 | 21 | 0 | 33 | 0 | 0 | 184 | 0 | 13 | 101 | 146 | 43 | 0 | 16 | 310 | 0 | 293 | 42 | 39 | 154 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6486 | 875 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 1452.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 160 | 48 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 55 | 220 | 0 | 600 | 570 | 17 | 6175.91 | 12661.91 | 102.06
06:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 17 | 17 | 130 | 48 | 15 | 0 | 0 | 0 | 0 | 120 | 370 | 0 | 0 | 315 | 0 | 0 | 0 | 123 | 17 | 21 | 0 | 0 | 99 | 16 | 19 | 0 | 18 | 0 | 23 | 0 | 12 | 12 | 0.05 | 220 | 92 | 21 | 780 | 17 | 0 | 50 | 0 | 102 | 188 | 0 | 0 | 0 | 1226 | 0 | 13 | 63 | 0 | 360 | 0 | 51 | 40 | 0 | 34 | 0 | 0 | 184 | 0 | 8 | 98 | 132 | 43 | 1 | 16 | 315 | 0 | 293 | 42 | 39 | 155 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 49 | 0.71 | 48 | 0 | 0.1 | 0.57 | 12 | 6512.43 | 875 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 1151.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0.22 | 0 | 0 | 0 | 0.02 | 155 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 163 | 48 | 35 | 1 | 0 | 0 | 0 | 0 | 0.6 | 11 | 0 | 16 | 307 | 55 | 220 | 0 | 600 | 550 | 17 | 5716.67 | 12229.1 | 102.08
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 17 | 17 | 130 | 48 | 15 | 0 | 0 | 0 | 0 | 120 | 375 | 0 | 0 | 305 | 0 | 0 | 3 | 140 | 17 | 22 | 0 | 0 | 100 | 16 | 19 | 0 | 18 | 0 | 23 | 0 | 12 | 12 | 0.3 | 221 | 90 | 19 | 780 | 16 | 0 | 50 | 0 | 94 | 187 | 0 | 0 | 0 | 1224 | 0 | 13 | 107 | 0 | 359 | 0 | 51 | 45 | 0 | 34 | 0 | 0 | 189 | 0 | 8 | 106 | 130 | 43 | 2 | 16 | 320 | 0 | 293 | 43 | 39 | 154 | 1 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 49 | 1.78 | 48 | 0 | 0.4 | 1.11 | 12 | 6584.59 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.36 | 1165 | 0 | 0 | 0 | 1004.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2.89 | 18 | 0 | 0 | 2.42 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0.41 | 161 | 48 | 35 | 2 | 0 | 0 | 0 | 0 | 1.6 | 44 | 0 | 16 | 307 | 60 | 220 | 0 | 600 | 450 | 17 | 5454.82 | 12039.41 | 102.12
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 17 | 17 | 130 | 15 | 14 | 0 | 0 | 0 | 0 | 120 | 360 | 0 | 0 | 296 | 0 | 0 | 7 | 143.42 | 15 | 22 | 0 | 0 | 52 | 16 | 18 | 0 | 13 | 0 | 0 | 17 | 12 | 12 | 0.72 | 220 | 68 | 20 | 790 | 0 | 0 | 50 | 0 | 51 | 187 | 0 | 0 | 0 | 1224 | 0 | 13 | 108 | 0 | 358 | 0 | 51 | 44 | 0 | 34 | 0 | 0 | 177 | 0 | 13 | 58 | 128 | 8 | 3 | 16 | 305 | 0 | 293 | 42 | 39 | 142 | 6 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 49 | 10.7 | 48 | 0 | 0.7 | 21.27 | 12 | 6316.81 | 875 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 1124 | 0 | 0 | 0 | 1101.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.37 | 13 | 0 | 0 | 8.45 | 153 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 1.37 | 161 | 50 | 35 | 7 | 0 | 0 | 0 | 0 | 2.4 | 58 | 0.01 | 16 | 307 | 60 | 180 | 0 | 600 | 405 | 8 | 5577.14 | 11893.95 | 102.12
09:00 | 0 | 34 | 26 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 17 | 17 | 131 | 0 | 14 | 0 | 0 | 0 | 0 | 120 | 345 | 0 | 0 | 310 | 0 | 0 | 12 | 143.42 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 1.2 | 222 | 0 | 20 | 780 | 0 | 0 | 21 | 0 | 0 | 105 | 0 | 0 | 0 | 1172 | 1 | 0 | 108 | 0 | 358 | 0 | 51 | 44 | 0 | 34 | 0 | 0 | 17 | 0 | 13 | 0 | 126 | 0 | 12 | 16 | 310 | 0 | 293 | 42 | 39 | 144 | 7 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 58 | 20.4 | 48 | 0 | 1.7 | 34.65 | 12 | 5772.37 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 1146 | 0 | 0 | 0 | 1149.28 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 28.93 | 48 | 0 | 0 | 27.87 | 176 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 163 | 50 | 0 | 25 | 0 | 0 | 0 | 0 | 3.1 | 77 | 0.07 | 0 | 277 | 60 | 220 | 0 | 600 | 404 | 0 | 5767.25 | 11539.62 | 102.14
10:00 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 17 | 130 | 0 | 13 | 0 | 0 | 0 | 0 | 120 | 310 | 0 | 0 | 280 | 0 | 0 | 21 | 143.42 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 2.64 | 222 | 0 | 20 | 840 | 0 | 0 | 19 | 0 | 0 | 106 | 0 | 0 | 0 | 1110 | 0 | 0 | 110 | 0 | 360 | 0 | 51 | 43 | 0 | 34 | 0 | 0 | 17 | 0 | 13 | 0 | 136 | 0 | 23 | 16 | 315 | 0 | 281 | 41 | 39 | 132 | 10 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 58 | 8 | 113 | 0 | 1.9 | 30.92 | 12 | 5819.88 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10.12 | 1157 | 0 | 0 | 0 | 1208.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.84 | 106 | 0 | 0 | 32.32 | 176 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 5.76 | 163 | 50 | 0 | 32 | 0 | 0 | 0 | 0 | 5.2 | 111 | 0.02 | 0 | 278 | 60 | 220 | 0 | 600 | 404 | 0 | 5940.4 | 11760.28 | 102.16
11:00 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 17 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 325 | 0 | 0 | 300 | 0 | 0 | 27 | 143.42 | 16 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 1.57 | 222 | 0 | 10 | 840 | 0 | 0 | 19 | 0 | 0 | 188 | 0 | 0 | 0 | 1170 | 1 | 0 | 110 | 0 | 347 | 0 | 51 | 44 | 0 | 34 | 0 | 0 | 17 | 0 | 13 | 0 | 142 | 0 | 36 | 16 | 310 | 0 | 237 | 41 | 39 | 142 | 2 | 8 | 0 | 22 | 0 | 0 | 0 | 104 | 17 | 58 | 11 | 116 | 0 | 0.9 | 18.19 | 12 | 5900.08 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 1147 | 0 | 0 | 0 | 1201.14 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 10.02 | 67 | 0 | 0 | 50.24 | 176 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 1.91 | 163 | 49 | 0 | 25 | 0 | 0 | 0 | 0 | 6.8 | 150 | 0.02 | 0 | 278 | 60 | 220 | 0 | 600 | 404 | 0 | 5897.13 | 11797.21 | 102.18
12:00 | 0 | 45 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 5 | 0 | 17 | 111 | 73 | 0 | 3 | 17 | 0 | 0 | 120 | 325 | 0 | 17 | 270 | 0 | 0 | 32 | 143.42 | 16 | 14 | 0 | 0 | 7 | 16 | 0 | 0 | 14 | 0 | 0 | 17 | 12 | 12 | 2.5 | 222 | 25 | 0 | 795 | 8 | 0 | 18 | 1 | 27 | 186 | 0 | 0 | 0 | 1224 | 2 | 10 | 108 | 0 | 353 | 0 | 51 | 43 | 0 | 33 | 13 | 0 | 95 | 0 | 13 | 98 | 148 | 6 | 31 | 16 | 315 | 0 | 237 | 41 | 39 | 148 | 10 | 8 | 0 | 22 | 0 | 0 | 0 | 103 | 17 | 58 | 9.1 | 116 | 0 | 0.9 | 46.2 | 12 | 6372.12 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 37 | 1162 | 0 | 0 | 0 | 1206.16 | 0 | 0 | 0 | 35 | 25 | 0 | 0 | 0 | 7 | 57.08 | 94 | 0 | 0 | 19.77 | 175 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 2.56 | 161 | 49 | 75 | 31 | 0 | 0 | 0 | 0 | 7.8 | 199 | 0.02 | 16 | 307 | 60 | 180 | 0 | 600 | 403 | 0 | 6128.39 | 12500.51 | 102.21
13:00 | 0 | 80 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 0 | 17 | 111 | 97 | 0 | 35 | 35 | 0 | 0 | 120 | 320 | 0 | 35 | 273 | 0 | 0 | 33 | 143.42 | 16 | 14 | 0 | 0 | 89 | 16 | 2 | 0 | 14 | 0 | 0 | 17 | 12 | 12 | 1.7 | 222 | 79 | 2 | 780 | 16 | 0 | 20 | 8 | 103 | 186 | 0 | 0 | 0 | 1224 | 10 | 26 | 108 | 0 | 353 | 0 | 51 | 42 | 0 | 33 | 37 | 0 | 147 | 0 | 13 | 102 | 154 | 40 | 36 | 16 | 310 | 0 | 235 | 41 | 39 | 142 | 12 | 8 | 0 | 22 | 0 | 0 | 0 | 101 | 17 | 58 | 11 | 116 | 0 | 1 | 53.63 | 12 | 6871.75 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 52.8 | 1162 | 0 | 0 | 0 | 1214.74 | 0 | 0 | 0 | 35 | 35 | 0 | 13 | 0 | 8 | 32.05 | 45 | 0 | 0 | 61.21 | 172 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 4.71 | 161 | 49 | 110 | 34 | 0 | 0 | 0 | 0 | 7.5 | 212 | 0.27 | 16 | 307 | 60 | 220 | 0 | 600 | 403 | 13 | 6298.28 | 13170.03 | 102.26
14:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 11 | 17 | 60 | 81 | 0 | 35 | 35 | 0 | 0 | 120 | 320 | 0 | 35 | 283 | 0 | 0 | 28 | 143.42 | 16 | 14 | 0 | 0 | 15 | 16 | 19 | 0 | 15 | 0 | 0 | 17 | 12 | 12 | 1.13 | 222 | 102 | 15 | 780 | 16 | 0 | 48 | 8 | 97 | 188 | 0 | 0 | 0 | 1100 | 8 | 24 | 108 | 0 | 351 | 0 | 51 | 42 | 0 | 32 | 51 | 0 | 187 | 0 | 13 | 70 | 146 | 0 | 37 | 16 | 310 | 0 | 236 | 41 | 39 | 140 | 8 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 58 | 18.24 | 116 | 0 | 2.3 | 36.83 | 12 | 6601.92 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 51.97 | 1143 | 0 | 0 | 0 | 1028.92 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 0 | 48.86 | 110 | 0 | 0 | 4.95 | 170 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0.91 | 162 | 49 | 90 | 34 | 0 | 0 | 0 | 0 | 5.2 | 168 | 0.25 | 16 | 227 | 60 | 220 | 0 | 600 | 440 | 17 | 5950.06 | 12551.98 | 102.27
15:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 0 | 60 | 81 | 0 | 35 | 35 | 0 | 0 | 120 | 325 | 0 | 35 | 285 | 0 | 0 | 17 | 143.42 | 17 | 14 | 0 | 0 | 26 | 16 | 18 | 0 | 20 | 0 | 0 | 17 | 12 | 12 | 0.93 | 222 | 104 | 5 | 780 | 18 | 0 | 50 | 8 | 99 | 186 | 0 | 0 | 0 | 1170 | 10 | 24 | 112 | 0 | 347 | 0 | 51 | 41 | 0 | 32 | 50 | 0 | 185 | 0 | 13 | 68 | 144 | 0 | 24 | 15 | 320 | 0 | 230 | 41 | 37 | 148 | 8 | 8 | 0 | 22 | 0 | 0 | 0 | 101 | 17 | 58 | 15.01 | 116 | 0 | 0.5 | 27.88 | 12 | 6643.74 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32 | 1135 | 0 | 0 | 0 | 929.97 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 0 | 23.2 | 50 | 0 | 0 | 22.95 | 175 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 2.9 | 161 | 47 | 90 | 24 | 0 | 0 | 0 | 0 | 3.5 | 167 | 0.14 | 16 | 276 | 60 | 220 | 0 | 600 | 530 | 17 | 5902.66 | 12546.4 | 102.3
16:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 10 | 60 | 81 | 0 | 35 | 35 | 0 | 0 | 120 | 320 | 0 | 35 | 270 | 0 | 0 | 3 | 143.42 | 19 | 14 | 0 | 0 | 47 | 16 | 18 | 0 | 23 | 0 | 0 | 17 | 12 | 12 | 0.69 | 222 | 102 | 13 | 780 | 18 | 0 | 50 | 8 | 97 | 186 | 0 | 0 | 0 | 1130 | 4 | 24 | 143 | 0 | 357 | 0 | 51 | 41 | 0 | 32 | 51 | 0 | 182 | 0 | 13 | 45 | 134 | 0 | 11 | 14 | 310 | 0 | 230 | 41 | 37 | 140 | 7 | 8 | 0 | 22 | 0 | 0 | 0 | 101 | 17 | 58 | 1 | 116 | 0 | 0.4 | 8.23 | 12 | 6542.74 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23 | 1162 | 0 | 0 | 0 | 908.04 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 0 | 1.56 | 61 | 0 | 0 | 28.33 | 175 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.77 | 162 | 47 | 50 | 11 | 28 | 0 | 0 | 0 | 2.1 | 113 | 0.09 | 32 | 276 | 60 | 180 | 0 | 600 | 560 | 17 | 5790.89 | 12333.63 | 102.34
17:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 30 | 45 | 81 | 0 | 35 | 35 | 0 | 0 | 120 | 305 | 0 | 35 | 285 | 0 | 0 | 8 | 143.42 | 19 | 14 | 0 | 0 | 15 | 16 | 20 | 0 | 29 | 0 | 0 | 17 | 12 | 12 | 0.32 | 222 | 68 | 20 | 780 | 16 | 0 | 50 | 8 | 34 | 186 | 0 | 0 | 0 | 1180 | 2 | 12 | 142 | 0 | 346 | 0 | 51 | 41 | 0 | 32 | 51 | 51 | 68 | 5 | 13 | 17 | 132 | 0 | 7 | 14 | 305 | 0 | 230 | 41 | 38 | 128 | 1 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 58 | 6.5 | 116 | 0 | 0.5 | 7.27 | 8 | 6329.01 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 1150 | 0 | 0 | 0 | 827.74 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13.76 | 21 | 0 | 0 | 15.23 | 175 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 1.65 | 162 | 47 | 0 | 7 | 30 | 0 | 0 | 0 | 1.3 | 54 | 0.03 | 16 | 283 | 60 | 180 | 0 | 600 | 555 | 17 | 5523.71 | 11852.72 | 102.38
18:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 35 | 17 | 50 | 45 | 81 | 0 | 35 | 34 | 0 | 0 | 120 | 305 | 0 | 35 | 275 | 0 | 0 | 2 | 143.42 | 15 | 21 | 0 | 0 | 15 | 16 | 22 | 0 | 40 | 10 | 0 | 17 | 12 | 12 | 0.04 | 222 | 67 | 23 | 835 | 16 | 0 | 50 | 8 | 33 | 186 | 0 | 0 | 0 | 1150 | 0 | 12 | 160 | 0 | 352 | 0 | 51 | 42 | 0 | 32 | 51 | 51 | 68 | 26 | 13 | 17 | 126 | 0 | 1 | 14 | 315 | 0 | 230 | 41 | 38 | 144 | 1 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 58 | 1.2 | 116 | 0 | 0.1 | 1.3 | 6 | 6446.06 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 1132 | 0 | 0 | 0 | 807.51 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 1 | 6.78 | 6 | 0 | 0 | 2.94 | 174 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0.34 | 162 | 47 | 0 | 1 | 34 | 0 | 0 | 0 | 0.6 | 7 | 0.01 | 16 | 210 | 60 | 220 | 0 | 600 | 550 | 17 | 5372.18 | 11818.24 | 102.42
19:00 | 0 | 51 | 30 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 54 | 17 | 63 | 113 | 81 | 0 | 35 | 116 | 0 | 0 | 120 | 330 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 15 | 21 | 0 | 0 | 43 | 16 | 34 | 0 | 39 | 50 | 23 | 54.36 | 12 | 12 | 0 | 221 | 77 | 30 | 1030 | 48 | 0 | 50 | 8 | 69 | 186 | 0 | 0 | 0 | 1224 | 0 | 20 | 181 | 0 | 353 | 0 | 51 | 43 | 0 | 32 | 68 | 50 | 112 | 26 | 13 | 57 | 156 | 9 | 0 | 14 | 320 | 0 | 292 | 41 | 39 | 148 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 59 | 0 | 123 | 0 | 0 | 0 | 10 | 7434.78 | 901 | 0 | 0 | 16 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1131 | 0 | 0 | 0 | 780.92 | 0 | 0 | 0 | 35 | 30 | 0 | 100 | 21 | 8 | 0 | 0 | 14 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 164 | 47 | 90 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 201 | 60 | 220 | 0 | 700 | 555 | 17 | 5773.92 | 13208.7 | 102.46
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 54 | 17 | 63 | 124 | 81 | 0 | 35 | 142 | 0 | 0 | 120 | 340 | 0 | 55 | 270 | 0 | 0 | 0 | 143.42 | 13 | 21 | 0 | 0 | 92 | 16 | 44 | 0 | 27 | 50 | 23 | 54.36 | 12 | 12 | 0 | 220 | 101 | 30 | 1105 | 120 | 0 | 50 | 8 | 100 | 186 | 0 | 0 | 0 | 1224 | 0 | 70 | 180 | 0 | 355 | 0 | 51 | 43 | 0 | 32 | 89 | 50 | 175 | 26 | 13 | 106 | 162 | 34 | 0 | 14 | 325 | 0 | 315 | 41 | 39 | 150 | 0 | 8 | 0 | 63 | 0 | 0 | 0 | 100 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 12 | 8123.78 | 901 | 0 | 0 | 31 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1152 | 0 | 0 | 0 | 786.23 | 0 | 0 | 0 | 57 | 70 | 0 | 100 | 26 | 8 | 0 | 0 | 14 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 166 | 47 | 104 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 202 | 60 | 220 | 0 | 982 | 570 | 35 | 6230.23 | 14354.01
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 54 | 17 | 61 | 134 | 81 | 0 | 35 | 146 | 0 | 0 | 120 | 335 | 0 | 55 | 270 | 0 | 0 | 0 | 143.42 | 14 | 22 | 0 | 0 | 96 | 16 | 43 | 0 | 46 | 50 | 23 | 54.36 | 12 | 12 | 0 | 220 | 107 | 30 | 1125 | 120 | 0 | 50 | 8 | 100 | 186 | 0 | 0 | 0 | 1190 | 0 | 60 | 180 | 0 | 360 | 0 | 51 | 44 | 0 | 33 | 89 | 50 | 177 | 27 | 13 | 106 | 152 | 43 | 0 | 14 | 310 | 0 | 317 | 40 | 39 | 145 | 0 | 8 | 0 | 63 | 0 | 0 | 0 | 100 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 12 | 8126.78 | 892 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1160 | 0 | 0 | 0 | 774.07 | 0 | 0 | 0 | 57 | 75 | 0 | 100 | 30 | 8 | 0 | 0 | 14 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 160 | 47 | 112 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 199 | 60 | 180 | 0 | 1050 | 570 | 35 | 6187.07 | 14313.85 | 102.52
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 54 | 17 | 68 | 143 | 81 | 0 | 35 | 144 | 0 | 0 | 120 | 315 | 0 | 55 | 270 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 92 | 16 | 43 | 0 | 38 | 50 | 23 | 54.36 | 12 | 12 | 0 | 220 | 106 | 34 | 1125 | 152 | 0 | 50 | 8 | 99 | 186 | 0 | 0 | 0 | 1190 | 0 | 50 | 180 | 0 | 356 | 0 | 51 | 44 | 0 | 33 | 88 | 50 | 178 | 27 | 13 | 105 | 164 | 43 | 0 | 14 | 310 | 0 | 305 | 40 | 39 | 146 | 0 | 8 | 0 | 63 | 0 | 0 | 0 | 100 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 12 | 8128.78 | 901 | 0 | 0 | 27 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1161 | 0 | 0 | 0 | 805.4 | 0 | 0 | 0 | 57 | 100 | 0 | 100 | 28 | 52.2 | 0 | 0 | 14 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 160 | 47 | 106 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 202 | 60 | 220 | 0 | 1050 | 570 | 35 | 6405.6 | 14534.38 | 102.58
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 71 | 142 | 81 | 0 | 35 | 144 | 0 | 0 | 120 | 325 | 0 | 55 | 290 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 94 | 16 | 45 | 0 | 30 | 50 | 23 | 54.36 | 12 | 12 | 0 | 220 | 107 | 34 | 1125 | 162 | 0 | 50 | 8 | 98 | 186 | 0 | 0 | 0 | 1190 | 0 | 50 | 180 | 0 | 358 | 0 | 51 | 44 | 0 | 33 | 89 | 50 | 184 | 27 | 13 | 105 | 168 | 52.2 | 0 | 21 | 315 | 0 | 305 | 41 | 39 | 151 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 69 | 0 | 155 | 0 | 0 | 0 | 12 | 8130.98 | 901 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 813.34 | 0 | 0 | 0 | 57 | 113 | 0 | 100 | 21 | 52.2 | 0 | 0 | 14 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 162 | 47 | 109 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 60 | 220 | 0 | 1050 | 565 | 35 | 6405.54 | 14536.52 | 102.64
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 61 | 142 | 81 | 0 | 35 | 108 | 0 | 0 | 120 | 330 | 0 | 35 | 280 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 100 | 16 | 44 | 0 | 20 | 50 | 23 | 17 | 12 | 12 | 0 | 220 | 110 | 33 | 1125 | 160 | 0 | 50 | 8 | 103 | 187 | 0 | 0 | 0 | 1192 | 0 | 50 | 185 | 0 | 358 | 0 | 51 | 45 | 0 | 30 | 69 | 50 | 187 | 27 | 19 | 103 | 158 | 52.2 | 0 | 23 | 320 | 0 | 305 | 40 | 39 | 150 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 69 | 0 | 155 | 0 | 0 | 0 | 12 | 8010.62 | 901 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 790.94 | 0 | 0 | 0 | 57 | 113 | 0 | 100 | 21 | 52.2 | 0 | 0 | 14 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 161 | 47 | 111 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 203 | 60 | 220 | 0 | 1050 | 570 | 35 | 6380.14 | 14390.76 | 102.7
Total KWH | 0 | 1359360 | 741600 | 0 | 0 | 0 | 0 | 0 | 7268400 | 0 | 0 | 324720 | 383760 | 719424 | 2781120 | 1630909 | 145680 | 604892 | 986400 | 0 | 0 | 2965411 | 8069091 | 0 | 469101 | 6996185 | 0 | 0 | 186025 | 3372000 | 388200 | 445680 | 0 | 0 | 1628400 | 331200 | 529920 | 0 | 522240 | 395396 | 296080 | 392238 | 351360 | 264000 | 13441 | 5318487 | 2008109 | 465600 | 20829090.91 | 946764 | 0 | 1079520 | 102430.8 | 1967127 | 4414040 | 0 | 0 | 0 | 28652725 | 38070 | 570400 | 2576000 | 0 | 8886000 | 0 | 1248609 | 900480 | 916000 | 817776 | 842880 | 379317 | 3610080 | 176400 | 319080 | 1811460 | 34442560 | 678173 | 232300 | 395200 | 7559000 | 0 | 6808000 | 963000 | 934320 | 3519000 | 70349 | 197808 | 0 | 625920 | 0 | 0 | 0 | 2433850 | 428760 | 1348800 | 123721 | 2265600 | 0 | 11900 | 298880 | 279120 | 197054939.71 | 21555636 | 0 | 0 | 139200 | 0 | 912000 | 0 | 0 | 0 | 0 | 37872 | 257040 | 27665460 | 0 | 0 | 0 | 26067129 | 0 | 0 | 0 | 384000 | 805728 | 0 | 653104 | 134931 | 295541 | 280768 | 628650 | 112000 | 0 | 288064 | 4223636 | 0 | 0 | 0 | 0 | 0 | 9033751 | 0 | 23820 | 4030000 | 1093964 | 1812552 | 230179 | 680476 | 0 | 0 | 0 | 47047.44 | 1376640 | 1326 | 356640 | 6523000 | 1603000 | 5320260 | 0 | 16596364 | 12699636.36 | 435600 | 146305014.8 | 343359954.51