## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 09-06-2026 | [28 empty] | Date: | 09-06-2026 | [28 empty] | Date: | 09-06-2026 | [28 empty] | Date: | 09-06-2026 | [28 empty] | Date: | 09-06-2026 | [18 empty] | Date: | 09-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [18 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 40 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 23 | 147 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 365 | 0 | 35 | 288 | 0 | 0 | 0 | 142 | 16 | 21 | 0 | 395 | 94 | 16 | 51 | 0 | 11 | 50 | 0 | 18 | 12 | 12 | 0 | 65 | 105 | 28 | 1120 | 67 | 0 | 50 | 26 | 90 | 221 | 0 | 0 | 0 | 1224 | 0 | 40 | 0 | 220 | 280 | 220 | 51 | 0 | 216 | 10 | 70 | 92 | 161 | 0 | 19 | 32 | 168 | 53 | 0 | 30 | 305 | 0 | 332 | 39 | 30 | 147 | 0 | 16 | 0 | 79 | 25 | 95 | 0 | 100 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 8157 | 932 | 133 | 0 | 24 | 40 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1191 | 0 | 0 | 0 | 1422 | 0 | 41 | 0 | 35 | 35 | 0 | 92 | 18 | 25 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 42 | 103 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 303 | 127 | 220 | 0 | 489 | 1228 | 35 | 7333 | 15490 | 74.17
01:00 | 0 | 17 | 40 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 17 | 147 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 365 | 0 | 0 | 290 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 410 | 95 | 16 | 28 | 0 | 3 | 50 | 0 | 18 | 12 | 12 | 0 | 65 | 106 | 20 | 1120 | 64 | 0 | 50 | 26 | 95 | 221 | 0 | 0 | 0 | 1162 | 0 | 40 | 0 | 220 | 280 | 220 | 51 | 0 | 214 | 10 | 65 | 92 | 174 | 0 | 19 | 33 | 164 | 53 | 0 | 30 | 315 | 0 | 332 | 28 | 30 | 151 | 0 | 16 | 0 | 79 | 25 | 95 | 0 | 100 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 8054 | 932 | 142 | 0 | 24 | 40 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1194 | 0 | 0 | 0 | 1430 | 0 | 41 | 0 | 35 | 35 | 0 | 0 | 18 | 25 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 40 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 293 | 127 | 220 | 0 | 498 | 1204 | 35 | 7246 | 15300 | 74.15
02:00 | 0 | 17 | 40 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 17 | 147 | 32 | 15 | 35 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 290 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 390 | 92 | 16 | 24 | 0 | 7 | 0 | 0 | 18 | 12 | 12 | 0 | 65 | 105 | 25 | 1120 | 34 | 0 | 50 | 26 | 96 | 221 | 0 | 0 | 0 | 1161 | 0 | 40 | 0 | 220 | 280 | 220 | 51 | 0 | 215 | 10 | 0 | 92 | 173 | 0 | 18 | 17 | 164 | 53 | 0 | 30 | 305 | 0 | 332 | 28 | 30 | 143 | 0 | 21 | 0 | 79 | 25 | 96 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7800 | 837 | 144 | 0 | 24 | 40 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1192 | 0 | 0 | 0 | 1389 | 0 | 41 | 0 | 35 | 35 | 0 | 0 | 18 | 25 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 41 | 90 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 276 | 127 | 220 | 0 | 487 | 1181 | 35 | 7035 | 14835 | 74.13
03:00 | 0 | 17 | 40 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 17 | 147 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 284 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 365 | 70 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 12 | 0 | 65 | 106 | 25 | 1120 | 0 | 0 | 50 | 0 | 97 | 221 | 0 | 0 | 0 | 1160 | 0 | 40 | 0 | 220 | 280 | 220 | 51 | 0 | 215 | 10 | 0 | 92 | 120 | 0 | 19 | 0 | 158 | 25 | 0 | 30 | 305 | 0 | 332 | 28 | 30 | 143 | 0 | 21 | 0 | 80 | 25 | 95 | 0 | 102 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7491 | 931 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1193 | 0 | 0 | 0 | 1353 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 43 | 90 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 256 | 127 | 220 | 0 | 460 | 1150 | 35 | 6769 | 14260 | 74.11
04:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 17 | 148 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 293 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 12 | 0 | 65 | 68 | 30 | 1120 | 0 | 0 | 26 | 0 | 96 | 221 | 0 | 0 | 0 | 1161 | 0 | 12 | 0 | 220 | 280 | 220 | 51 | 0 | 216 | 10 | 0 | 93 | 34 | 0 | 19 | 0 | 156 | 0 | 0 | 14 | 310 | 0 | 332 | 28 | 30 | 145 | 0 | 21 | 0 | 80 | 25 | 95 | 0 | 102 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7256 | 932 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1195 | 0 | 0 | 0 | 1362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 45 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 127 | 220 | 0 | 457 | 1140 | 0 | 6596 | 13852 | 74.09
05:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 17 | 148 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 293 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 395 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 34 | 32 | 1120 | 0 | 0 | 0 | 0 | 68 | 222 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 220 | 280 | 220 | 51 | 0 | 218 | 10 | 0 | 92 | 0 | 0 | 19 | 0 | 148 | 0 | 0 | 0 | 305 | 0 | 332 | 28 | 30 | 146 | 0 | 21 | 0 | 80 | 25 | 0 | 0 | 103 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6972 | 932 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1194 | 0 | 0 | 0 | 1350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 127 | 220 | 0 | 469 | 1106 | 0 | 6530 | 13502 | 74.07
06:00 | 0 | 17 | 40 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 17 | 148 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 297 | 0 | 0 | 2 | 142 | 17 | 21 | 0 | 415 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 0 | 32 | 1120 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1160 | 1 | 0 | 0 | 220 | 280 | 220 | 51 | 0 | 217 | 10 | 0 | 92 | 0 | 0 | 19 | 0 | 150 | 0 | 7 | 0 | 310 | 0 | 337 | 28 | 30 | 138 | 0 | 21 | 0 | 80 | 25 | 0 | 0 | 102 | 0 | 49 | 1 | 48 | 0 | 0 | 1 | 0 | 6885 | 932 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1197 | 0 | 0 | 0 | 1282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 0 | 0 | 2 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 1 | 0 | 44 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 237 | 127 | 220 | 0 | 429 | 1048 | 0 | 6362 | 13247 | 74.05
07:00 | 0 | 17 | 40 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 17 | 148 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 293 | 0 | 0 | 4 | 142 | 16 | 21 | 0 | 395 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 0 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1160 | 5 | 0 | 0 | 220 | 280 | 220 | 51 | 0 | 218 | 10 | 0 | 90 | 0 | 0 | 19 | 0 | 140 | 0 | 13 | 0 | 305 | 0 | 337 | 28 | 30 | 148 | 0 | 0 | 0 | 80 | 25 | 0 | 0 | 104 | 0 | 49 | 2 | 48 | 0 | 1 | 3 | 0 | 6849 | 932 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1199 | 0 | 0 | 0 | 1298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | 0 | 0 | 5 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 1 | 0 | 44 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 245 | 127 | 220 | 0 | 464 | 1050 | 0 | 6477 | 13326 | 74.03
08:00 | 0 | 17 | 40 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 17 | 128 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 290 | 0 | 0 | 10 | 105 | 16 | 21 | 0 | 370 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 62 | 0 | 2 | 1120 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 10 | 0 | 0 | 250 | 280 | 250 | 51 | 0 | 198 | 10 | 0 | 90 | 0 | 0 | 12 | 0 | 148 | 0 | 34 | 0 | 305 | 0 | 337 | 28 | 30 | 138 | 1 | 0 | 0 | 80 | 30 | 0 | 0 | 103 | 0 | 49 | 5 | 46 | 0 | 1 | 4 | 0 | 6783 | 932 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 1163 | 0 | 0 | 0 | 1249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 29 | 0 | 0 | 14 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 2 | 0 | 45 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 216 | 127 | 220 | 0 | 408 | 1040 | 0 | 6342 | 13125 | 74.01
09:00 | 0 | 17 | 42 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 17 | 150 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 295 | 0 | 0 | 22 | 105 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 2 | 1120 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1165 | 10 | 0 | 0 | 250 | 280 | 250 | 51 | 0 | 201 | 10 | 0 | 90 | 0 | 0 | 12 | 0 | 150 | 0 | 19 | 0 | 310 | 0 | 344 | 28 | 30 | 142 | 3 | 0 | 0 | 82 | 30 | 0 | 0 | 102 | 0 | 49 | 17 | 46 | 0 | 2 | 33 | 0 | 6864 | 932 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 1060 | 0 | 0 | 0 | 1232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 61 | 0 | 0 | 18 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 2 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 3 | 28 | 1 | 0 | 205 | 127 | 220 | 0 | 373 | 1030 | 0 | 6267 | 13131 | 73.99
10:00 | 0 | 17 | 42 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 17 | 0 | 20 | 150 | 25 | 15 | 0 | 35 | 0 | 0 | 0 | 370 | 0 | 17 | 290 | 0 | 0 | 26 | 105 | 0 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 3 | 57 | 0 | 2 | 1125 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1160 | 10 | 0 | 0 | 250 | 280 | 250 | 43 | 0 | 200 | 10 | 0 | 88 | 0 | 0 | 19 | 0 | 154 | 0 | 20 | 0 | 305 | 0 | 344 | 28 | 30 | 149 | 9 | 16 | 0 | 82 | 30 | 0 | 0 | 102 | 0 | 49 | 10 | 46 | 0 | 0 | 31 | 0 | 7042 | 932 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 1060 | 0 | 0 | 0 | 1263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 67 | 0 | 0 | 1 | 0 | 0 | 140 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 43 | 0 | 4 | 0 | 0 | 0 | 0 | 3 | 8 | 1 | 0 | 240 | 127 | 220 | 0 | 461 | 1035 | 0 | 6444 | 13486 | 73.97
11:00 | 0 | 25 | 42 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 17 | 0 | 20 | 147 | 32 | 15 | 17 | 72 | 0 | 0 | 0 | 365 | 0 | 17 | 293 | 0 | 0 | 22 | 105 | 0 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 8 | 3 | 57 | 0 | 2 | 1125 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1160 | 6 | 1 | 0 | 280 | 280 | 250 | 43 | 0 | 201 | 10 | 0 | 88 | 0 | 0 | 19 | 0 | 158 | 0 | 31 | 0 | 310 | 0 | 344 | 28 | 30 | 137 | 5 | 16 | 0 | 82 | 30 | 0 | 0 | 102 | 0 | 49 | 1 | 48 | 0 | 0 | 2 | 0 | 7125 | 931 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 1056 | 0 | 0 | 0 | 1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 70 | 0 | 0 | 9 | 0 | 0 | 140 | 0 | 130 | 0 | 414 | 0 | 1 | 0 | 44 | 0 | 18 | 0 | 0 | 0 | 0 | 4 | 204 | 1 | 0 | 258 | 127 | 220 | 0 | 496 | 1080 | 0 | 6732 | 13857 | 73.96
12:00 | 0 | 34 | 42 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 17 | 0 | 35 | 147 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 366 | 0 | 0 | 298 | 0 | 0 | 12 | 105 | 0 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 12 | 12 | 3 | 59 | 18 | 2 | 1125 | 0 | 0 | 22 | 0 | 34 | 214 | 0 | 0 | 0 | 1190 | 13 | 46 | 0 | 280 | 280 | 270 | 43 | 0 | 203 | 10 | 1 | 88 | 1 | 1 | 19 | 0 | 164 | 1 | 30 | 0 | 310 | 0 | 344 | 28 | 30 | 136 | 3 | 16 | 0 | 82 | 30 | 0 | 0 | 102 | 0 | 58 | 1 | 67 | 0 | 1 | 12 | 0 | 7367 | 932 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 1077 | 0 | 0 | 0 | 1282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 42 | 0 | 0 | 25 | 0 | 0 | 140 | 0 | 130 | 0 | 414 | 0 | 3 | 0 | 45 | 0 | 10 | 0 | 0 | 0 | 0 | 6 | 200 | 1 | 0 | 264 | 127 | 220 | 0 | 478 | 1100 | 0 | 6774 | 14141 | 73.96
13:00 | 0 | 17 | 42 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 17 | 0 | 35 | 97 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 370 | 0 | 0 | 315 | 0 | 0 | 23 | 68 | 0 | 14 | 0 | 410 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 12 | 5 | 60 | 60 | 2 | 1125 | 0 | 0 | 25 | 0 | 102 | 213 | 0 | 0 | 0 | 1160 | 5 | 98 | 0 | 250 | 280 | 270 | 43 | 0 | 192 | 10 | 31 | 87 | 60 | 18 | 19 | 0 | 160 | 37 | 59 | 22 | 320 | 0 | 344 | 28 | 30 | 136 | 8 | 16 | 0 | 82 | 30 | 10 | 0 | 102 | 0 | 58 | 5 | 67 | 0 | 1 | 24 | 0 | 7623 | 932 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 1175 | 0 | 0 | 0 | 1441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 0 | 31 | 0 | 0 | 140 | 0 | 140 | 0 | 403 | 0 | 3 | 0 | 46 | 0 | 11 | 0 | 0 | 0 | 0 | 5 | 160 | 1 | 0 | 274 | 127 | 220 | 0 | 495 | 1110 | 0 | 7006 | 14629 | 73.96
14:00 | 0 | 17 | 42 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 35 | 100 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 375 | 0 | 0 | 296 | 0 | 0 | 23 | 68 | 16 | 21 | 0 | 375 | 2 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 12 | 12 | 3 | 60 | 66 | 2 | 1125 | 6 | 0 | 25 | 3 | 103 | 213 | 0 | 0 | 0 | 1160 | 10 | 95 | 0 | 250 | 320 | 51 | 51 | 0 | 221 | 10 | 35 | 87 | 96 | 10 | 19 | 0 | 164 | 53 | 51 | 29 | 310 | 0 | 344 | 28 | 30 | 146 | 0 | 16 | 0 | 83 | 30 | 10 | 0 | 102 | 0 | 59 | 8 | 67 | 0 | 2 | 36 | 0 | 7551 | 932 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 1200 | 0 | 0 | 0 | 1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 20 | 0 | 0 | 24 | 0 | 0 | 149 | 0 | 140 | 0 | 352 | 0 | 3 | 0 | 44 | 80 | 18 | 33 | 0 | 0 | 0 | 4 | 146 | 1 | 0 | 254 | 127 | 220 | 0 | 467 | 1146 | 0 | 7086 | 14637 | 73.96
15:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 35 | 115 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 290 | 0 | 0 | 19 | 86 | 16 | 21 | 0 | 400 | 17 | 0 | 8 | 0 | 34 | 0 | 0 | 0 | 12 | 12 | 3 | 60 | 65 | 2 | 1125 | 28 | 0 | 26 | 26 | 100 | 213 | 0 | 0 | 0 | 1164 | 12 | 45 | 0 | 320 | 320 | 55 | 51 | 0 | 201 | 10 | 34 | 87 | 150 | 8 | 19 | 20 | 168 | 53 | 41 | 29 | 310 | 0 | 344 | 28 | 30 | 151 | 0 | 16 | 0 | 83 | 30 | 10 | 0 | 102 | 0 | 59 | 11 | 67 | 0 | 1 | 32 | 8 | 7711 | 932 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 1200 | 0 | 0 | 0 | 1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 16 | 34 | 0 | 0 | 31 | 0 | 0 | 152 | 0 | 140 | 0 | 401 | 0 | 4 | 0 | 41 | 91 | 14 | 33 | 0 | 0 | 0 | 2 | 58 | 1 | 0 | 268 | 122 | 220 | 0 | 502 | 1180 | 0 | 7080 | 14791 | 73.96
16:00 | 0 | 35 | 42 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 34 | 148 | 32 | 0 | 35 | 35 | 0 | 0 | 0 | 330 | 0 | 10 | 297 | 0 | 0 | 3 | 105 | 16 | 21 | 0 | 330 | 13 | 0 | 31 | 0 | 20 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 66 | 2 | 1125 | 48 | 0 | 26 | 26 | 98 | 213 | 0 | 0 | 0 | 1145 | 8 | 20 | 0 | 250 | 320 | 103 | 51 | 0 | 192 | 10 | 35 | 87 | 173 | 9 | 0 | 32 | 144 | 53 | 32 | 29 | 305 | 0 | 344 | 0 | 0 | 131 | 1 | 16 | 0 | 83 | 30 | 118 | 0 | 102 | 0 | 59 | 7 | 67 | 0 | 1 | 23 | 12 | 7499 | 932 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 1195 | 0 | 0 | 0 | 1455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 2 | 20 | 0 | 0 | 12 | 0 | 0 | 152 | 0 | 140 | 0 | 333 | 0 | 2 | 0 | 41 | 95 | 7 | 34 | 0 | 0 | 0 | 2 | 28 | 1 | 0 | 206 | 122 | 220 | 0 | 352 | 1164 | 0 | 6717 | 14216
17:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 34 | 148 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 293 | 0 | 0 | 0 | 105 | 16 | 21 | 0 | 340 | 15 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 12 | 1 | 0 | 34 | 2 | 1125 | 17 | 0 | 25 | 26 | 68 | 213 | 0 | 0 | 0 | 977 | 2 | 20 | 0 | 250 | 320 | 103 | 51 | 0 | 197 | 10 | 34 | 94 | 51 | 26 | 0 | 17 | 88 | 53 | 11 | 30 | 305 | 0 | 344 | 0 | 0 | 127 | 0 | 16 | 0 | 83 | 30 | 141 | 0 | 102 | 0 | 59 | 2 | 67 | 0 | 1 | 10 | 12 | 7001 | 932 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 1124 | 0 | 0 | 0 | 1450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 2 | 11 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 140 | 0 | 340 | 0 | 1 | 0 | 41 | 50 | 5 | 34 | 0 | 0 | 0 | 2 | 32 | 1 | 0 | 199 | 100 | 180 | 0 | 349 | 1030 | 0 | 6212 | 13213
18:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 36 | 0 | 42 | 131 | 32 | 0 | 35 | 35 | 0 | 0 | 0 | 325 | 0 | 35 | 293 | 0 | 0 | 0 | 105 | 16 | 19 | 0 | 345 | 13 | 0 | 42 | 0 | 6 | 0 | 0 | 0 | 12 | 12 | 1 | 0 | 32 | 0 | 1050 | 0 | 0 | 28 | 26 | 68 | 213 | 0 | 0 | 0 | 910 | 0 | 20 | 0 | 220 | 290 | 103 | 51 | 0 | 196 | 10 | 34 | 95 | 17 | 26 | 0 | 0 | 116 | 16 | 0 | 30 | 305 | 0 | 344 | 0 | 0 | 129 | 0 | 16 | 0 | 83 | 30 | 141 | 0 | 102 | 0 | 59 | 1 | 67 | 0 | 0 | 2 | 12 | 6842 | 932 | 156 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 980 | 1 | 0 | 0 | 1453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1 | 7 | 0 | 0 | 4 | 0 | 0 | 130 | 0 | 130 | 0 | 338 | 0 | 1 | 0 | 41 | 50 | 2 | 34 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 201 | 100 | 180 | 0 | 349 | 1000 | 0 | 6119 | 12961
19:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 36 | 0 | 72 | 131 | 32 | 0 | 35 | 54 | 0 | 0 | 0 | 345 | 0 | 35 | 294 | 0 | 0 | 0 | 113 | 16 | 19 | 0 | 390 | 15 | 16 | 44 | 0 | 6 | 50 | 0 | 1 | 12 | 12 | 0 | 0 | 36 | 9 | 940 | 6 | 0 | 50 | 26 | 85 | 213 | 0 | 0 | 0 | 1120 | 0 | 35 | 0 | 220 | 290 | 103 | 51 | 0 | 220 | 20 | 40 | 94 | 18 | 26 | 6 | 15 | 124 | 16 | 0 | 30 | 310 | 0 | 356 | 0 | 0 | 134 | 0 | 25 | 0 | 83 | 30 | 142 | 0 | 102 | 1 | 68 | 0 | 86 | 0 | 0 | 0 | 0 | 7361 | 932 | 155 | 0 | 27 | 51 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 932 | 17 | 0 | 0 | 1458 | 0 | 18 | 0 | 10 | 2 | 0 | 92 | 25 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 396 | 0 | 0 | 0 | 41 | 90 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 225 | 126 | 220 | 0 | 442 | 1005 | 9 | 6650 | 14011
19:30 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 36 | 0 | 73 | 131 | 32 | 0 | 35 | 54 | 0 | 0 | 0 | 319 | 0 | 35 | 286 | 0 | 0 | 0 | 123 | 16 | 19 | 0 | 330 | 15 | 16 | 44 | 0 | 7 | 50 | 0 | 14 | 12 | 12 | 0 | 0 | 49 | 6 | 840 | 0 | 0 | 50 | 26 | 95 | 217 | 0 | 0 | 0 | 1150 | 0 | 150 | 0 | 220 | 290 | 103 | 51 | 0 | 220 | 30 | 90 | 95 | 100 | 26 | 7 | 0 | 126 | 16 | 0 | 30 | 305 | 0 | 356 | 0 | 0 | 136 | 0 | 25 | 0 | 0 | 30 | 140 | 0 | 102 | 17 | 68 | 0 | 85 | 0 | 0 | 0 | 0 | 7373 | 932 | 155 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1086 | 17 | 0 | 0 | 1449 | 0 | 40 | 0 | 50 | 22 | 0 | 92 | 25 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 336 | 0 | 0 | 0 | 41 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 126 | 220 | 0 | 500 | 1100 | 4 | 6932 | 14305
20:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 36 | 0 | 74 | 133 | 32 | 0 | 35 | 54 | 0 | 0 | 0 | 330 | 0 | 35 | 282 | 0 | 0 | 0 | 142 | 16 | 19 | 0 | 320 | 0 | 0 | 44 | 0 | 14 | 50 | 0 | 22 | 12 | 12 | 0 | 0 | 98 | 12 | 1000 | 0 | 0 | 50 | 26 | 94 | 218 | 0 | 0 | 0 | 1160 | 0 | 50 | 0 | 220 | 290 | 103 | 51 | 0 | 220 | 35 | 88 | 95 | 34 | 27 | 7 | 0 | 128 | 0 | 0 | 15 | 310 | 0 | 356 | 0 | 0 | 130 | 0 | 25 | 0 | 83 | 30 | 142 | 0 | 102 | 17 | 69 | 0 | 87 | 0 | 0 | 0 | 0 | 7509 | 932 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1128 | 17 | 0 | 0 | 1452 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 326 | 0 | 0 | 0 | 41 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 126 | 220 | 0 | 500 | 1124 | 0 | 6896 | 14405
21:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 35.5 | 0 | 63 | 149 | 32 | 0 | 35 | 54 | 0 | 0 | 0 | 325 | 0 | 35 | 292 | 0 | 0 | 0 | 142 | 16 | 20 | 0 | 360 | 0 | 0 | 48 | 0 | 8 | 50 | 0 | 0 | 12 | 12 | 0 | 0 | 50 | 16 | 1125 | 0 | 0 | 25 | 25.5 | 51 | 218 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 220 | 290 | 18 | 51 | 0 | 220 | 37 | 34 | 95 | 0 | 0 | 7 | 0 | 130 | 0 | 0 | 0 | 305 | 0 | 356 | 0 | 0 | 130 | 0 | 25 | 0 | 83 | 30 | 142 | 0 | 102 | 17 | 69 | 0 | 87 | 0 | 0 | 0 | 0 | 7271 | 932 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1202 | 17 | 0 | 0 | 1455 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 349 | 0 | 0 | 0 | 42 | 115 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 126 | 220 | 0 | 500 | 1190 | 0 | 7061 | 14332
22:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 35.5 | 0 | 37 | 135 | 32 | 0 | 35 | 54 | 0 | 0 | 0 | 340 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 16 | 19 | 0 | 395 | 0 | 0 | 50 | 0 | 2 | 44 | 0 | 0 | 12 | 12 | 0 | 0 | 51 | 21 | 1125 | 0 | 0 | 26 | 25.5 | 48 | 218 | 0 | 0 | 0 | 937 | 0 | 0 | 0 | 290 | 290 | 58 | 51 | 0 | 220 | 39 | 30 | 94 | 0 | 0 | 13 | 0 | 116 | 0 | 0 | 0 | 310 | 0 | 356 | 0 | 0 | 134 | 0 | 25 | 0 | 83 | 30 | 142 | 0 | 102 | 17 | 69 | 0 | 91 | 0 | 0 | 0 | 0 | 7175 | 932 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1204 | 17 | 0 | 0 | 1453 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 377 | 0 | 0 | 0 | 42 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 126 | 220 | 0 | 500 | 1200 | 0 | 7104 | 14279
23:00 | 0 | 34 | 42 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 19 | 0 | 17 | 138 | 32 | 0 | 35 | 54 | 0 | 0 | 0 | 375 | 0 | 0 | 310 | 0 | 0 | 0 | 142 | 15.5 | 19 | 0 | 440 | 11 | 0 | 50 | 0 | 15 | 50 | 0 | 0 | 12 | 12 | 0 | 0 | 60 | 27 | 1125 | 0 | 0 | 26 | 25.5 | 58 | 217 | 0 | 0 | 0 | 510 | 0 | 8 | 0 | 330 | 290 | 58 | 51 | 7 | 132 | 39 | 37 | 93 | 0 | 0 | 19 | 0 | 132 | 0 | 0 | 0 | 315 | 0 | 356 | 0 | 0 | 152 | 0 | 25 | 0 | 83 | 30 | 144 | 0 | 103 | 17 | 69 | 0 | 93 | 0 | 0 | 0 | 0 | 6798 | 932 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 17 | 0 | 0 | 1456 | 0 | 0 | 0 | 10 | 2 | 0 | 84 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 42 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 126 | 220 | 0 | 500 | 1210 | 0 | 7161 | 13959
Total KWH | 0 | 988800 | 983520 | 0 | 0 | 0 | 0 | 0 | 8546400 | 0 | 0 | 261360 | 0 | 745200 | 3348480 | 600676 | 238916 | 533086 | 812160 | 0 | 0 | 0 | 8570834 | 0 | 269273 | 7125194 | 0 | 0 | 158411 | 3003600 | 336600 | 455400 | 0 | 9265000 | 511855 | 62727 | 469440 | 0 | 359040 | 338696 | 0 | 101284 | 195840 | 212160 | 15617 | 0 | 1346500 | 300000 | 26625454.55 | 286036 | 0 | 577440 | 313732.8 | 1619199 | 5173269 | 0 | 0 | 0 | 26181816 | 99495 | 744363 | 0 | 6068500 | 7411500 | 4046000 | 1218544 | 32640 | 5001000 | 383544 | 585600 | 2166162 | 1332480 | 157080 | 354570 | 150480 | 3450240 | 480979 | 309245 | 338848 | 7521000 | 0 | 8360000 | 0 | 0 | 3379745.46 | 24611 | 416304 | 0 | 1967040 | 680064 | 1558000 | 0 | 2459100 | 76320 | 1339200 | 63885 | 1483200 | 0 | 5600 | 210000 | 47040 | 174855395.81 | 22440000 | 3841920 | 0 | 70560 | 128256 | 0 | 0 | 0 | 0 | 0 | 144144 | 631440 | 27592730 | 102240 | 0 | 0 | 0 | 0 | 132356 | 0 | 183456 | 210048 | 0 | 517984 | 83787 | 51163 | 257584 | 531800 | 201446 | 0 | 194864 | 0 | 0 | 3508136 | 0 | 3458127 | 0 | 9432509 | 0 | 18120 | 0 | 983563 | 1354811 | 108597 | 658867 | 0 | 0 | 0 | 36503.04 | 829440 | 4081 | 77760 | 6196000 | 2974000 | 5697310 | 0 | 10952727 | 27499636.36 | 132000 | 131237965.4 | 306093361.21

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 10-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-06-2026 | during | 10-06-2026 | during | 10-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 378 | 328 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 0 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 298 | 282 | 335 | 335 | 310 | 310 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 36 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 147 | 133 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 16 | 33 | 33 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 19 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 42 | 42 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 32 | 300 | 300 | 33 | 33 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 74 | 149 | 149 | 35 | 72 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 34 | 51 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 54 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 12 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 320 | 584 | 584 | 430 | 430 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 366 | 330 | 583 | 583 | 380 | 380 | AGC+Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 105 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2002 | 1983 | 5820.22 | 5792.22 | 2096.36 | 2337.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 26 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 22 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 59 | 57 | 65 | 65 | 65 | 65 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 218 | 215 | 215 | 215 | 215 | Machine Problem
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 94 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 8 | 8 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 12 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 44 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3 | 0 | 4.72 | 0 | 4.72 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 22 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 18 | 98 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 35 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1190 | 1160 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 4 | 14 | 25 | 21 | 25 | 21 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 1000 | 1150 | 1150 | 1150 | 1150 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2708 | 2869 | 3945.58 | 3985.86 | 3163.22 | 3351.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 203 | 220 | 221.25 | 221.25 | 215 | 215 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 280 | 290 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 270 | 103 | 342.01 | 342.01 | 342.01 | 342.01 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 280 | 220 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 35 | 41.65 | 41.65 | 11 | 11 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 46 | 50 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 15 | 40 | 40 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 88 | 95 | 163 | 163 | 94 | 94 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 1 | 34 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 164 | 128 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 1 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 7 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 1 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 88 | 115 | 115 | 34 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 30 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1437 | 1363 | 2757.44 | 2698.44 | 2141.22 | 2268.22
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-06-2026 | during | 10-06-2026 | during | 10-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 1 | 0 | 10 | 0 | 10 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 67 | 87 | 70 | 90 | 70 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 69 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 12 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 139 | 173 | 478.7 | 446.5 | 209.2 | 189
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 28 | 28 | 28 | 28 | 28 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Plant availability less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 136 | 130 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 142 | 150 | 150 | 100 | 100 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 83 | 83 | 83 | 83 | 83 | one engine under maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 102 | 101 | 101 | 101 | 101 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 25 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 344 | 356 | 350 | 350 | 350 | 350 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1081 | 1236 | 1301 | 1301 | 1201.02 | 1201.02
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 932 | 932 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 39 | 39 | 39 | 39 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 155 | 156 | 410 | 410 | 170 | 170 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 50 | 50 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 100 | 0 | 60 | 0 | 60 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1077 | 1128 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2264 | 2233 | 3569.2 | 3509.2 | 2545 | 2485
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 478 | 500 | 500 | 500 | 500 | 500 | AGC, Unit1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 127 | 126 | 130 | 130 | 130 | 130 | STG Under Maintenance
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1100 | 1124 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 0 | 90 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 264 | 307 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2190 | 2277 | 2662 | 2661 | 2338 | 2427
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 23 | 0 | 57 | 0 | 57 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 130 | 220 | 220 | 140 | 140 | Gas Restrction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 130 | 220 | 220 | 130 | 130 | Gas Restrction
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 326 | 413.79 | 413.79 | 413.79 | 413.79 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1282 | 1452 | 1435.88 | 1435.88 | 1356 | 1356 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 25 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 42 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2059 | 2160 | 3017.57 | 2793.87 | 2487.69 | 2385.99
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 45 | 41 | 0 | 0 | 41 | 41 | Plant availability zero, U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 35 | 100 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 200 | 0 | 104.67 | 0 | 104.67 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 261 | 226 | 338.67 | 228 | 301.67 | 256
System Total |  |  |  |  | 28843.2 | 29290.237 | 14141 | 14520 | 23890.38 | 23416.09 | 16483.38 | 16901.09
Forecast Scenario (10-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15820 |  | 0 |  | 15820
|  |  |  | 1:00 | 15300 |  | 0 |  | 15300
|  |  |  | 2:00 | 14940 |  | 0 |  | 14940
|  |  |  | 3:00 | 14530 |  | 0 |  | 14530
|  |  |  | 4:00 | 14120 |  | 0 |  | 14120
|  |  |  | 5:00 | 13860 |  | 0 |  | 13860
|  |  |  | 6:00 | 13370 |  | 0 |  | 13370
|  |  |  | 7:00 | 13470 |  | 0 |  | 13470
|  |  |  | 8:00 | 13480 |  | 0 |  | 13480
|  |  |  | 9:00 | 13680 |  | 0 |  | 13680
|  |  |  | 10:00 | 14070 |  | 0 |  | 14070
|  |  |  | 11:00 | 14410 |  | 0 |  | 14410
|  |  |  | 12:00 | 15140 |  | 0 |  | 15140
|  |  |  | 13:00 | 15100 |  | 0 |  | 15100
|  |  |  | 14:00 | 15160 |  | 0 |  | 15160
|  |  |  | 15:00 | 15600 |  | 0 |  | 15600
|  |  |  | 16:00 | 15480 |  | 0 |  | 15480
|  |  |  | 17:00 | 15090 |  | 0 |  | 15090
|  |  |  | 18:00 | 14480 |  | 0 |  | 14480
|  |  |  | 18:30 | 15000 |  | 0 |  | 15000
|  |  |  | 19:00 | 15580 |  | 0 |  | 15580
|  |  |  | 19:30 | 16250 |  | 0 |  | 16250
|  |  |  | 20:00 | 15930 |  | 0 |  | 15930
|  |  |  | 21:00 | 15910 |  | 0 |  | 15910
|  |  |  | 22:00 | 15760 |  | 0 |  | 15760
|  |  |  | 23:00 | 15720 |  | 0 |  | 15720
Probable Maximum Temperature: |  |  | 37.40°C
Probable Maximum Demand at Day Peak: |  |  | 15140.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16250.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15796.51 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 354.86451 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:37 hrs on 10-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 09-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14141 | MW | 12:00 Hr. | Energy Generated |  |  | 306.0934 |  | MKWHr.
| Day Peak Demand |  |  | 14194.3 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.644 |  | MKWHr.
| Evening Peak Generation |  |  | 14520 | MW | 20:00 Hr. | Energy Demand |  |  | 308.7374 |  | MKWHr.
| Evening Peak Demand |  |  | 14707.06 | MW | 20:00 Hr. | Maximum Temperature |  |  | 34.3 |  | °C
| Minimum Generation of the Day |  |  | 13125 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 916.72 |  | MMCFD
| Maximum Generation of the Day |  |  | 15490 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.2772 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.2994 | 0 | 11.7851 | 0 | 0 | 0.15841 | 0 | 0 | 46.2429 | Gas | 121.7084 | Gas | 422280262.5832
| Chattogram Zone |  |  | 5.4733 | 52.8073 | 6.0349 | 0 | 0 | 0.11511 | 0 | 0.35904 | 64.7896 | Coal | 126.0319 | Coal | 829319454.3375
| Cumilla Zone |  |  | 26.6825 | 0 | 3.7898 | 0 | 0 | 0.30924 | 3.4502 | 0 | 34.2318 | HFO | 28.6044 | HFO | 494458488.216
| Mymensingh Zone |  |  | 0 | 0 | 2.9458 | 0 | 0 | 0.27948 | 0 | 0 | 3.2252 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.3413 | 0 | 0 | 0 | 0 | 0.024611 | 0 | 0 | 26.3659 | Hydro | 0 | Hydro | 0
| Khulna Zone |  |  | 3.8419 | 27.5927 | 0.4452 | 0 | 0 | 0.63144 | 22.44 | 0 | 54.9513 | Solar | 3.4993 | Solar | 55602074.7408
| Barishal Zone |  |  | 8.6713 | 44.6484 | 0.20976 | 0 | 0 | 0.004081 | 0 | 0 | 53.5335 | Import | 25.8902 | Import | 114459417.6
| Rajshahi Zone |  |  | 16.3988 | 0 | 1.3802 | 0 | 0 | 1.0024 | 0 | 0 | 18.7814 | Wind | 0.35904 | Wind | 5281478.4
| Rangpur Zone |  |  | 0 | 0.98356 | 2.0137 | 0 | 0 | 0.97454 | 0 | 0 | 3.9718
| Total |  |  | 121.7084 | 126.0319 | 28.6044 | 0 | 0 | 3.4993 | 25.8902 | 0.35904 | 306.0934
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 422280262.5832 |  | Hydro | 0
|  |  |  | Coal | 829319454.3375 |  | Solar | 55602074.7408
|  |  |  | HFO | 494458488.216 |  | Import | 114459417.6
|  |  |  | HSD | 0 |  | Wind | 5281478.4
[5 empty] | Total: | 192,14,01,175 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.44 | Peak Hr Flow | 932.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51854709.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: |  | Peak Hr Flow | 1452.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2458 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.4502 | Peak Hr Flow | 128.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2610 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 25.8902 | Peak Hr Flow | 2512.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5444
|  |  |  | Chattogram |  | 0 |  | 1520
|  |  |  | Cumilla |  | 0 |  | 1131
|  |  |  | Mymensingh |  | 179 |  | 1253
|  |  |  | Sylhet |  | 0 |  | 533
|  |  |  | Khulna |  | 0 |  | 1487
|  |  |  | Barishal |  | 0 |  | 351
|  |  |  | Rajshahi |  | 0 |  | 1485
|  |  |  | Rangpur |  | 0 |  | 1013
|  |  |  | Total |  | 179 |  | 14217
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:29 | 08:53 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Forced S/D Due to PBS auxiliary transformer | [7 empty] | 20.0MW load
|  |  | replace | [7 empty] | interrup.
| 08:30 | 08:53 | Niamatpur 132/33kV S/S Transformer-1(407T) HT Forced S/D Due to PBS auxiliary transformer | [7 empty] | 20.0MW load
|  |  | replace | [7 empty] | interrup.
| 08:34 | 18:46 | Maijdee 132/33kV S/S Chowmuhoni-Maijdee ckt -01 Project Work S/D Due to Project work
| 08:35 | 18:45 | Chowmuhani 230/132/33kV S/S Maijdee-01 Project Work S/D
| 09:06 | 19:41 | Barguna 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Replacement of Circuit Breaker
of T2-A Incomer.
| 09:06 | 19:40 | Barguna 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Replacement of Circuit Breaker
of T2-A Incomer
| 09:50 | 12:56 | Niamatpur 132/33kV S/S Transformer-3(426T) LT Scheduled S/D Due to T-3 33 kV source bus
DS maintenance work
| 09:51 | 12:55 | Niamatpur 132/33kV S/S Transformer-3(426T) HT Scheduled S/D Due to T-3 33kv source bus DS
maintenance work
| 10:54 | 19:49 | Lalmonirhat-Rangpur 132 kV Ckt-2 Scheduled S/D from Lalmonirhat 132/33kV end Due to
Installation of distance relay
|  | 11:03 | Satkhira 132/33kV S/S Transformer-3(T-3) HT is restored.
|  | 11:06 | Satkhira 132/33kV S/S Transformer-3(T-3) LT is restored.
| 11:12 | 14:19 | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to taken by
kaliyakair via NLDC
| 11:16 | 11:43 | Maijdee 132/33kV S/S Tr-02 HT Project Work S/D Due to project work
| 11:32 |  | Haripur 230/132kV S/S 132kV Bus Coupler-2 Scheduled S/D Due to 132kV CRP Panel Shifting
work from 100MW BPDB Control Room to 230/132kV Grid SS Control Room
| 11:33 | 14:48 | Barishal 230/132kV S/S ATR-2 LT Scheduled S/D Due to WTI change
| 11:34 | 14:50 | Barishal 230/132kV S/S ATR-2 HT Scheduled S/D Due to WTI change
| 11:57 | 12:14 | Maijdee 132/33kV S/S TR-01 HT Project Work S/D Due to 132/33 kV Tr-02 HT S/D due to
project work
| 12:00 |  | Day Peak Generation: 14131 MW.
| 13:03 | 19:57 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing OC/EF, RYB ph
Trip, d-51.8 km, AR blocked relays. and from Kabirpur 132/33kV end showing Distance Relay
relays.
| 13:18 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- ST
| 13:22 | 18:26 | Ashuganj-Brahmanbaria 132kV Ckt-2 Tripped from Brahmanbaria 132/33kV end showing Distance
relay relays.
| 13:30 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- False SMS ( STG Trip & GT Running
).
| 13:30 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- False SMS (STG Trip & GT
Running).
| 13:40 | 13:41 | Shikalbaha 230/132kV S/S ATR 02 HT Tripped showing FN1 relays Due to DC MCB trip.
| 13:41 | 14:02 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Tripped showing No Signal at Relay relays | [7 empty] | 58.0MW load
|  |  | Due to Due to Sikalbaha 230 KV Transformer Trip | [7 empty] | interrup.
|  | 14:14 | Kaliakoir-Kodda(300MW) 230kV Ckt-1 is restored.
|  | 15:43 | Meghnaghat 400/230kV S/S 230kV BUS Section 02 is restored.
|  | 15:45 | Meghnaghat 230/132kV S/S Bus2 is restored.
|  | 15:45 | Meghnaghat 230/132kV S/S Bus2 is restored.
| 16:21 | 19:57 | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end.
| 16:33 | 17:25 | Cumilla(N)-Cumilla(S) 132 kV Ckt-3 Tripped from Cumilla(S) 132/33kV end showing REL670
relays Due to Storm
| 16:52 | 17:17 | Madaripur 132/33kV S/S T2-415T LT Tripped showing O/C relays Due to Due to pbs Agoiljhara
fedder CT flash.
| 16:52 | 17:16 | Madaripur 132/33kV S/S T1-405T LT Tripped showing O/C relays Due to Due to pbs Agoiljhara
fedder CT flash.
| 21:45 | 22:30 | Faridpur 132/33kV S/S 33 KV Bus Scheduled S/D Due to WZPDCO 33 kv Feeder Red-hot
Maintenance. (33 kv Bus section-2, No 132 kv X-former Shutdown)
| 22:16 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST trip-22:16 on 09.6.26
| 22:16 |  | Ashuganj CCPP 225 MW Tripped with remarks:- ST
| 22:17 |  | Ashuganj 225 MW CCPP ST tripped.
| 22:31 |  | SS Power Tripped
| 22:31 |  | SS Power Synchronized with remarks:- u-2 tripped-22:31 on 09.06.26
| 22:31 |  | SS Power Bashkhali Unit-2 tripped.
| 22:45 |  | Daganbhuiyan 132/33kV S/S Transformer-2 LT Tripped showing Main Relay -01 relays Due to
PBS 33KV side B phase PT Broken & R phase conductor Broken
| 00:17 |  | Ashuganj South 360 MW CCPP ST was sync.
| 00:17 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 00:57 | 01:13 | Khagrachori 132/33kV S/S TR-2 LT Tripped showing REF630 relays Due to Due to crackdown of | [7 empty] | 22.0MW load
|  |  | Panchari 33 kV bus DS insulator. | [7 empty] | interrup.
| 00:57 | 01:13 | Khagrachori 132/33kV S/S TR-1 LT Tripped showing REF630 relays Due to Due to crackdown of | [7 empty] | 22.0MW load
|  |  | Panchari 33 kV bus DS insulator. | [7 empty] | interrup.
| 01:56 |  | SS Power Synchronized
| 01:56 |  | SS Power Bashkhali Unit-2 was sync.
| 02:30 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 02:30 |  | Ashuganj 225 MW CCPP ST was sync.
| 06:15 | 07:02 | Lalmonirhat 132/33kV S/S T-1 (425T) LT Scheduled S/D Due to T-01 33KV incoming circuit
breaker Red Hot maintenance
| 06:16 | 07:01 | Lalmonirhat 132/33kV S/S T-1 (425T) HT Scheduled S/D Due to T-01 33KV incoming circuit
breaker Red Hot maintenance
| 06:20 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to 33 kV bus Section DS, Babuganj & | [7 empty] | 58.0MW load
|  |  | Jhalakathi 33 kV feeder source DS Work. Work done by PBS | [7 empty] | interrup.
| 06:21 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to 33 kV bus Section DS, Babuganj & | [7 empty] | 58.0MW load
|  |  | Jhalakathi 33 kV feeder source DS Work. Work done by PBS | [7 empty] | interrup.
| 06:21 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to 33 kV bus Section DS, Babuganj & | [7 empty] | 58.0MW load
|  |  | Jhalakathi 33 kV feeder source DS Work. Work done by PBS | [7 empty] | interrup.
| 06:21 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to 33 kV bus Section DS, Babuganj & | [7 empty] | 58.0MW load
|  |  | Jhalakathi 33 kV feeder source DS Work. Work done by PBS | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 09-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 328 | 8546400 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 238916 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 282 | 7125194 | AGC+Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 36 | 261360 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 133 | 3348480 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 533086 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 269273 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16 | 336600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 19 | 455400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 42 | 983520 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 32 | 600676 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 74 | 745200 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 988800 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 812160 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 158411 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 320 | 9265000 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 330 | 8570834 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3003600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1983 | 46242910
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 26 | 313732.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 99495 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 577440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 57 | 0 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5173269 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 94 | 1619199 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 338696 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 195840 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 12 | 300000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 44 | 469440 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 15617 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 62727 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 22 | 101284 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 98 | 1346500 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 212160 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 511855 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 286036 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 26181816 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 14 | 359040 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1000 | 26625454.55 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2869 | 64789601.35
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 220 | 5001000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7411500 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 103 | 4046000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 6068500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 383544 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 32640 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1218544 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 744363 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 15 | 338848 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 95 | 2166162 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 1332480 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 128 | 3450240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 480979 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 7 | 354570 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 150480 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 157080 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 88 | 585600 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 309245 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1363 | 34231775
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 63885 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1483200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 1339200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 210000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 47040 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 76320 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 173 | 3225245
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 24611 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 0 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 0 | Plant availability less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3379745.46 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 1558000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 680064 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1967040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2459100 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 25 | 416304 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7521000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 356 | 8360000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1236 | 26365864.46
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 932 | 22440000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 70560 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 128256 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 156 | 3841920 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 102240 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 144144 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 631440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1128 | 27592730 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2233 | 54951290
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 500 | 10952727 | Unit1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 77760 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 126 | 2974000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1124 | 27499636.36 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5697310 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 132000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6196000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4081 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2277 | 53533514.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 257584 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 132356 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 83787 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 130 | 3508136 | Gas Restrction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 130 | 3458127 | Gas Restrction
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 326 | 9432509 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 201446 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 51163 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 517984 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 210048 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 183456 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 18120 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1452 | 0 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 194864 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 531800 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2160 | 18781380
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 41 | 983563 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 658867 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 36503.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1354811 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 108597 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 829440 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 226 | 3971781.04
Eastern Grid Total |  |  |  |  | 17438.042 | 7624 | 174855395.81
Western Grid Total |  |  |  |  | 11852.195 | 6896 | 131237965.4
National Grid Total |  |  |  |  | 29290.237 | 14520 | 306093361.21
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 09-06-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9758.21 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4335.8 | MW
i) Dhaka area |  |  | 5443.81 |  | MW | i) Khulna area |  |  |  | 1487 | MW
ii) Chattogram area |  |  | 1576.4 |  | MW | ii) Barishal area |  |  |  | 351.2 | MW
iii) Cumilla area |  |  | 1131 |  | MW | iii) Rajshahi area |  |  |  | 1484.6 | MW
iv) Mymensingh area |  |  | 1074 |  | MW | iv) Rangpur area |  |  |  | 1013 | MW
v) Sylhet area |  |  | 533 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14094.01 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 90 | 14:00 | 133 | Natore | 164 | 19:30
2 | AKSML | 156.4 | 16:00 | 68 | Hathazari | 91 | 00:00 | 134 | Nawabganj | 63.4 | 00:00
3 | Aftabnagar | 46 | 13:00 | 69 | Hatirjheel | 42 | 11:00 | 135 | Netrakona | 135 | 19:00
4 | Agargaon | 128 | 13:00 | 70 | Ishurdi | 85 | 19:30 | 136 | New | 84 | 12:00
5 | Agrabad | 76 | 16:00 | 71 | Jaldhaka | 84 | 22:00 | 137 | Niamatpur | 81 | 00:00
6 | Amnura | 47 | 04:00 | 72 | Jamalpur | 129 | 02:00 | 138 | Noapara | 62 | 19:30
7 | Ashuganj | 96 | 00:00 | 73 | Jashore | 153 | 23:00 | 139 | PHP | 14 | 12:00
8 | BSRM | 197 | 06:00 | 74 | Jhenaidah | 110 | 17:00 | 140 | Pabna | 104 | 00:00
9 | Bagerhat | 102 | 19:00 | 75 | Joydebpur | 152 | 17:00 | 141 | Palashbari | 130 | 19:30
10 | Bajitpur | 92 | 19:30 | 76 | Joypurhat | 66 | 22:00 | 142 | Panchagarh | 63 | 19:30
11 | Bakerganj | 16 | 19:00 | 77 | Juldah | 16 | 15:00 | 143 | Patiya | 11 | 19:30
12 | Bakulia | 108 | 14:00 | 78 | KSRM | 11 | 04:00 | 144 | Patuakhali | 76 | 20:00
13 | Banani | 61.6 | 13:00 | 79 | Kabirpur | 260 | 21:00 | 145 | Payra | 36 | 20:00
14 | Bangabhaban | 22 | 10:00 | 80 | Kachua | 98 | 00:00 | 146 | Postogola | 61 | 00:00
15 | Barapukuria | 68 | 20:00 | 81 | Kaliganj | 22 | 15:00 | 147 | Pubail | 27 | 16:00
16 | Barguna | 23 | 19:00 | 82 | Kallyanpur | 126 | 00:00 | 148 | Purbachal | 36 | 12:00
17 | Barishal | 122 | 19:00 | 83 | Kalurghat | 44 | 16:00 | 149 | Purbasadipur | 142 | 20:00
18 | Barishal-230 | 98 | 00:00 | 84 | Kamrangirchar | 76 | 13:00 | 150 | Rahanpur | 42 | 00:00
19 | Baroaulia | 54 | 15:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 47 | 18:00
20 | Baroirhat | 69 | 00:00 | 86 | Kasba | 39 | 00:00 | 152 | Rajbari | 94 | 00:00
21 | Bashundhara | 201 | 12:00 | 87 | Kazla | 115 | 12:00 | 153 | Rajendrapur | 114 | 03:00
22 | BashundharaCement | 12 | 00:00 | 88 | Keranigonj | 80 | 15:00 | 154 | Rajshahi | 122 | 00:00
23 | Beanibazar | 72 | 23:00 | 89 | Khagrachori | 30 | 01:00 | 155 | Rajshahi-230 | 114 | 13:00
24 | Benapole | 76 | 14:00 | 90 | Khulna | 74 | 13:00 | 156 | Ramganj | 116 | 00:00
25 | Bhaluka | 152 | 16:00 | 91 | Khulshi | 193 | 19:00 | 157 | Rampur | 42 | 15:00
26 | Bhandaria | 60 | 21:00 | 92 | Kishoreganj | 129 | 08:00 | 158 | Rangamati | 18 | 19:00
27 | Bhangura | 43 | 19:30 | 93 | Kodda | 313 | 10:00 | 159 | Rangpur | 140 | 21:00
28 | Bheramara(GK) | 71 | 20:00 | 94 | Kulaura | 49 | 00:00 | 160 | Ruppur | 4.6 | 09:00
29 | Bhulta | 212 | 11:00 | 95 | Kurigram | 70 | 20:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 86 | 00:00 | 96 | Kushtia | 176 | 13:00 | 162 | Saidpur | 103 | 20:00
31 | Bogura | 170 | 21:00 | 97 | Laksam | 29 | 23:00 | 163 | Santhia | 36 | 00:00
32 | Borhanuddin | 85 | 00:00 | 98 | Lakshmipur | 41 | 02:00 | 164 | Satkhira | 164 | 22:00
33 | Brahmanbaria | 142 | 00:00 | 99 | Lalbag | 76 | 13:00 | 165 | Satmasjid | 111 | 13:00
34 | Cantonment | 148 | 13:00 | 100 | Lalmonirhat | 66 | 22:00 | 166 | Savar | 222 | 15:00
35 | Chandina | 47 | 01:00 | 101 | MI_Cement | 15.2 | 11:00 | 167 | SevenRings | 12.53 | 01:00
36 | Chandpur | 90 | 02:00 | 102 | Madanganj | 32 | 11:00 | 168 | ShahCement | 42 | 07:00
37 | Chandraghona | 31 | 00:00 | 103 | Madaripur | 124 | 00:00 | 169 | Shahjadpur | 80 | 01:00
38 | Chapai | 81 | 12:00 | 104 | Madartek | 90 | 00:00 | 170 | Shahjibazar | 124 | 00:00
39 | Charsaidpur | 37 | 14:00 | 105 | Madunaghat | 58 | 15:00 | 171 | Shahmirpur | 62 | 00:00
40 | Chauddagram | 78 | 01:00 | 106 | Magura | 69 | 00:00 | 172 | Shariatpur | 97 | 01:00
41 | Chhatak | 36 | 02:00 | 107 | Mahasthangarh | 92 | 00:00 | 173 | Sherpur | 130 | 22:00
42 | Chowmuhani | 166 | 00:00 | 108 | Maijdee | 43 | 00:00 | 174 | Shikalbaha | 28 | 13:00
43 | Chuadanga | 123 | 23:00 | 109 | Manikganj | 138 | 02:00 | 175 | Shitalakhya | 84.4 | 15:00
44 | Coxsbazar | 143 | 19:00 | 110 | Maniknagar | 82 | 13:00 | 176 | Sholosohor | 46 | 19:00
45 | Cumilla(N) | 127 | 00:00 | 111 | Matarbari | 57 | 19:30 | 177 | Shomvuganj | 18 | 01:00
46 | Cumilla(S) | 168 | 00:00 | 112 | Matuail | 86 | 12:00 | 178 | Shyampur | 146 | 00:00
47 | Daganbhuiyan | 36 | 00:00 | 113 | Metrorail_Motijheel | 23 | 19:00 | 179 | Siddhirganj | 134 | 12:00
48 | Daudkandi | 139 | 00:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 108 | 00:00
49 | DhakaUniversity | 94 | 13:00 | 115 | Millgate | 103 | 16:00 | 181 | Sonargaon | 140 | 01:00
50 | Dhamrai | 110 | 00:00 | 116 | Mirpur | 151 | 15:00 | 182 | Sreemongol | 87 | 00:00
51 | Dhanmondi | 113.6 | 14:00 | 117 | Mirsorai | 44 | 12:00 | 183 | Sreepur | 117 | 21:00
52 | Dohazari | 106 | 18:30 | 118 | Mirzapur | 43 | 06:00 | 184 | Srinagar | 50.9 | 00:00
53 | Faridpur | 187 | 00:00 | 119 | Mithapukur | 64 | 19:30 | 185 | Sunamganj | 58 | 21:00
54 | Fatullah | 92 | 15:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 74 | 14:00
55 | Fenchuganj | 41 | 00:00 | 121 | Mogbazar | 109.3 | 12:00 | 187 | Sylhet-132 | 94 | 19:00
56 | Feni | 107 | 00:00 | 122 | Mongla | 43 | 11:00 | 188 | TK | 26 | 23:00
57 | GPH | 72 | 12:00 | 123 | Motijheel | 57 | 13:00 | 189 | Tangail | 170 | 06:00
58 | Ghatail | 98 | 06:00 | 124 | Muktagacha | 38 | 06:00 | 190 | Taraganj | 27 | 19:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 104 | 03:00 | 191 | Tasnim | 35 | 11:00
60 | Ghorashal-230 | 103 | 07:00 | 126 | Muradnagar | 50 | 00:00 | 192 | Thakurgaon | 111 | 20:00
61 | Goalpara | 42 | 19:30 | 127 | Mymensingh | 189 | 00:00 | 193 | Tongi | 160 | 10:00
62 | Gollamari | 116 | 19:00 | 128 | Nabinagar | 94 | 07:00 | 194 | Ullahpara | 41 | 19:30
63 | Gopalganj | 119 | 00:00 | 129 | Naogaon | 151 | 00:00 | 195 | Ullon | 59 | 00:00
64 | Gulshan | 148 | 13:00 | 130 | Narail | 58 | 01:00 | 196 | Uttara | 103 | 13:00
65 | Halishahar | 106.5 | 14:00 | 131 | Narinda | 74 | 13:00 | 197 | UttaraNew | 58 | 00:00
66 | HaripurSBU | 140 | 15:00 | 132 | Narshingdi | 182 | 00:00 | 198 | Zigatola | 84 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 09-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15490 | 585 |  | 16101.33
1:00 | 15300 | 314 |  | 15628.13
2:00 | 14835 | 193 |  | 15036.69
3:00 | 14260 | 174 |  | 14441.83
4:00 | 13852 | 159 |  | 14018.16
5:00 | 13502 | 153 |  | 13661.89
6:00 | 13247 | 46 |  | 13295.07
7:00 | 13326 | 26 |  | 13353.17
8:00 | 13125 | 20 |  | 13145.9
9:00 | 13131 | 20 |  | 13151.9
10:00 | 13486 | 15 |  | 13501.68
11:00 | 13857 | 45 |  | 13904.03
12:00 | 14141 | 51 |  | 14194.3
13:00 | 14629 | 30 |  | 14660.35
14:00 | 14637 | 10 |  | 14647.45
15:00 | 14791 | 80 |  | 14874.6
16:00 | 14334 | 75 |  | 14412.38
17:00 | 13331 | 15 |  | 13346.68
18:00 | 13078 | 27 |  | 13106.22
19:00 | 14127 | 101 |  | 14232.55
19:30 | 14421 | 121 |  | 14547.45
20:00 | 14520 | 179 |  | 14707.06
21:00 | 14446 | 108 |  | 14558.86
22:00 | 14392 | 108 |  | 14504.86
23:00 | 14075 | 110 |  | 14189.95
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 09-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8157 | 7333 | 15490 | DAILY GENERATION CURVE
00:30 | 8105.5 | 7289.5 | 15395
01:00 | 8054 | 7246 | 15300 | 09-06-2026
01:30 | 7927 | 7140.5 | 15067.5
02:00 | 7800 | 7035 | 14835
02:30 | 7645.5 | 6902 | 14547.5
03:00 | 7491 | 6769 | 14260
03:30 | 7373.5 | 6682.5 | 14056
04:00 | 7256 | 6596 | 13852
04:30 | 7114 | 6563 | 13677
05:00 | 6972 | 6530 | 13502
05:30 | 6928.5 | 6446 | 13374.5
06:00 | 6885 | 6362 | 13247
06:30 | 6867 | 6419.5 | 13286.5
07:00 | 6849 | 6477 | 13326
07:30 | 6816 | 6409.5 | 13225.5
08:00 | 6783 | 6342 | 13125
08:30 | 6823.5 | 6304.5 | 13128
09:00 | 6864 | 6267 | 13131
09:30 | 6953 | 6355.5 | 13308.5
10:00 | 7042 | 6444 | 13486
10:30 | 7083.5 | 6588 | 13671.5
11:00 | 7125 | 6732 | 13857
11:30 | 7246 | 6753 | 13999
12:00 | 7367 | 6774 | 14141
12:30 | 7495 | 6890 | 14385
13:00 | 7623 | 7006 | 14629
13:30 | 7587 | 7046 | 14633
14:00 | 7551 | 7086 | 14637
14:30 | 7631 | 7083 | 14714
15:00 | 7711 | 7080 | 14791
15:30 | 7664 | 6898.5 | 14562.5
16:00 | 7617 | 6717 | 14334
16:30 | 7368 | 6464.5 | 13832.5
17:00 | 7119 | 6212 | 13331
17:30 | 7039 | 6165.5 | 13204.5
18:00 | 6959 | 6119 | 13078
18:30 | 7218 | 6384.5 | 13602.5
19:00 | 7477 | 6650 | 14127
19:30 | 7489 | 6932 | 14421
20:00 | 7624 | 6896 | 14520
20:30 | 7504.5 | 6978.5 | 14483 |  | Executive Engineer
21:00 | 7385 | 7061 | 14446 |  | Network Operation Division
21:30 | 7336.5 | 7082.5 | 14419
22:00 | 7288 | 7104 | 14392
22:30 | 7101 | 7132.5 | 14233.5
23:00 | 6914 | 7161 | 14075

## En-Curve
QF-LDC-12
Date | 09-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3466 | 1662 | 932 | 0 | 168 | 1422 | 65 | 5597 | 0 | 715 | 1452 | 0 | 0 | 11 | 585 | DAILY ENERGY CURVE
00:30 | 3470.5 | 1673 | 932 | 0 | 166 | 1426 | 65 | 5554 | 0 | 669 | 1432.5 | 0 | 0 | 7 | 449.5 | 09-06-2026
01:00 | 3475 | 1684 | 932 | 0 | 164 | 1430 | 65 | 5511 | 0 | 623 | 1413 | 0 | 0 | 3 | 314
01:30 | 3469 | 1664.5 | 884.5 | 0 | 164 | 1409.5 | 65 | 5484.5 | 0 | 598 | 1323.5 | 0 | 0 | 5 | 253.5 | Energy Generated | 306.0934 |  | MKWHr
02:00 | 3463 | 1645 | 837 | 0 | 164 | 1389 | 65 | 5458 | 0 | 573 | 1234 | 0 | 0 | 7 | 193 | Energy not Served | 2.644 |  | MKWHr
02:30 | 3462.5 | 1636 | 884 | 0 | 161 | 1371 | 65 | 5420 | 0 | 474.5 | 1062.5 | 0 | 0 | 11 | 183.5 | Total Energy Requirement | 308.7374 |  | MKWHr
03:00 | 3462 | 1627 | 931 | 0 | 158 | 1353 | 65 | 5382 | 0 | 376 | 891 | 0 | 0 | 15 | 174
03:30 | 3469.5 | 1648 | 931.5 | 0 | 157 | 1357.5 | 65 | 5378 | 0 | 365 | 666.5 | 0 | 0 | 18 | 166.5
04:00 | 3477 | 1669 | 932 | 0 | 156 | 1362 | 65 | 5374 | 0 | 354 | 442 | 0 | 0 | 21 | 159
04:30 | 3434 | 1668 | 932 | 0 | 152 | 1356 | 65 | 5363 | 0 | 347 | 336.5 | 0 | 0 | 23.5 | 156
05:00 | 3391 | 1667 | 932 | 0 | 148 | 1350 | 65 | 5352 | 0 | 340 | 231 | 0 | 0 | 26 | 153
05:30 | 3387 | 1670.5 | 932 | 0 | 149 | 1316 | 65 | 5293.5 | 14 | 343.5 | 180 | 0 | 0 | 24 | 99.5
06:00 | 3383 | 1674 | 932 | 0 | 150 | 1282 | 65 | 5235 | 28 | 347 | 129 | 0 | 0 | 22 | 46
06:30 | 3392 | 1644.5 | 932 | 0 | 145 | 1290 | 65 | 5258.5 | 59.5 | 347 | 129 | 0 | 0 | 24 | 36
07:00 | 3401 | 1615 | 932 | 0 | 140 | 1298 | 65 | 5282 | 91 | 347 | 129 | 0 | 0 | 26 | 26
07:30 | 3411.5 | 1585 | 932 | 0 | 144 | 1273.5 | 63.5 | 5217 | 131.5 | 318.5 | 128 | 0 | 0 | 21 | 23
08:00 | 3422 | 1555 | 932 | 0 | 148 | 1249 | 62 | 5152 | 172 | 290 | 127 | 0 | 0 | 16 | 20
08:30 | 3430.5 | 1554.5 | 932 | 0 | 149 | 1240.5 | 61 | 5074.5 | 244.5 | 302 | 127 | 0 | 0 | 12.5 | 20
09:00 | 3439 | 1554 | 932 | 0 | 150 | 1232 | 60 | 4997 | 317 | 314 | 127 | 0 | 0 | 9 | 20
09:30 | 3446 | 1587 | 932 | 0 | 152 | 1247.5 | 58.5 | 5060.5 | 324 | 314 | 175.5 | 0 | 0 | 11.5 | 17.5
10:00 | 3453 | 1620 | 932 | 0 | 154 | 1263 | 57 | 5124 | 331 | 314 | 224 | 0 | 0 | 14 | 15
10:30 | 3475.5 | 1614 | 931.5 | 0 | 156 | 1264.5 | 57 | 5171.5 | 407 | 316.5 | 266 | 0 | 0 | 12 | 30
11:00 | 3498 | 1608 | 931 | 0 | 158 | 1266 | 57 | 5219 | 483 | 319 | 308 | 0 | 0 | 10 | 45
11:30 | 3509.5 | 1608 | 931.5 | 0 | 161 | 1274 | 58 | 5249 | 484 | 323.5 | 393.5 | 0 | 0 | 7 | 48
12:00 | 3521 | 1608 | 932 | 0 | 164 | 1282 | 59 | 5279 | 485 | 328 | 479 | 0 | 0 | 4 | 51
12:30 | 3508 | 1620 | 932 | 0 | 162 | 1361.5 | 59.5 | 5332 | 484 | 287 | 632.5 | 0 | 0 | 6.5 | 40.5
13:00 | 3495 | 1632 | 932 | 0 | 160 | 1441 | 60 | 5385 | 483 | 246 | 786 | 0 | 0 | 9 | 30
13:30 | 3393.5 | 1633 | 932 | 0 | 162 | 1447.5 | 60 | 5390.5 | 475.5 | 251 | 866 | 0 | 0 | 22 | 20
14:00 | 3292 | 1634 | 932 | 0 | 164 | 1454 | 60 | 5396 | 468 | 256 | 946 | 0 | 0 | 35 | 10
14:30 | 3340.5 | 1651.5 | 932 | 0 | 166 | 1451 | 60 | 5438 | 390 | 270.5 | 980 | 0 | 0 | 34.5 | 45
15:00 | 3389 | 1669 | 932 | 0 | 168 | 1448 | 60 | 5480 | 312 | 285 | 1014 | 0 | 0 | 34 | 80
15:30 | 3376 | 1587 | 932 | 0 | 156 | 1451.5 | 60 | 5354 | 253.5 | 325 | 1040.5 | 0 | 0 | 27 | 77.5
16:00 | 3363 | 1505 | 932 | 0 | 144 | 1455 | 60 | 5228 | 195 | 365 | 1067 | 0 | 0 | 20 | 75
16:30 | 3284 | 1483 | 932 | 0 | 116 | 1452.5 | 60 | 5036.5 | 152 | 400.5 | 901.5 | 0 | 0 | 14.5 | 45
17:00 | 3205 | 1461 | 932 | 0 | 88 | 1450 | 60 | 4845 | 109 | 436 | 736 | 0 | 0 | 9 | 15
17:30 | 3236 | 1465 | 932 | 0 | 102 | 1451.5 | 59.5 | 4688 | 70 | 433 | 760 | 0 | 0 | 7.5 | 21
18:00 | 3267 | 1469 | 932 | 0 | 116 | 1453 | 59 | 4531 | 31 | 430 | 784 | 0 | 0 | 6 | 27
18:30 | 3351 | 1538.5 | 932 | 0 | 120 | 1455.5 | 58.5 | 4618 | 15.5 | 579.5 | 928 | 0 | 0 | 6 | 64
19:00 | 3435 | 1608 | 932 | 0 | 124 | 1458 | 58 | 4705 | 0 | 729 | 1072 | 0 | 0 | 6 | 101
19:30 | 3340 | 1434 | 932 | 0 | 126 | 1449 | 58 | 4977 | 0 | 670 | 1428 | 0 | 0 | 7 | 121
20:00 | 3347 | 1523 | 932 | 0 | 128 | 1452 | 57 | 5260 | 0 | 609 | 1198 | 0 | 0 | 14 | 179
20:30 | 3318.5 | 1540.5 | 932 | 0 | 129 | 1453.5 | 56.5 | 5393 | 0 | 609.5 | 1039.5 | 0 | 0 | 11 | 143.5
21:00 | 3290 | 1558 | 932 | 0 | 130 | 1455 | 56 | 5526 | 0 | 610 | 881 | 0 | 0 | 8 | 108
21:30 | 3365 | 1592.5 | 932 | 0 | 123 | 1454 | 55.5 | 5420.5 | 0 | 600 | 871.5 | 0 | 0 | 5 | 108
22:00 | 3440 | 1627 | 932 | 0 | 116 | 1453 | 55 | 5315 | 0 | 590 | 862 | 0 | 0 | 2 | 108
22:30 | 3451 | 1687.75 | 932 | 0 | 124 | 1454.5 | 56.5 | 5108.5 | 0 | 555 | 855.75 | 0 | 0 | 8.5 | 109
23:00 | 3462 | 1748.5 | 932 | 0 | 132 | 1456 | 58 | 4902 | 0 | 520 | 849.5 | 0 | 0 | 15 | 110
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 09-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 177 | 49 | 510 | 200 | 1678 | 572 | Ishurdi-Ghorashal Ckt-1 | Export | 4150036.36
1:00 | 164 | 38 | 510 | 200 | 1700 | 534
2:00 | 155 | 44 | 480 | 190 | 1622 | 526 |  | Import | 0
3:00 | 160 | 37 | 470 | 184 | 1546 | 516
4:00 | 174 | 39 | 528 | 182 | 1630 | 528 | Ishurdi-Ghorashal Ckt-2 | Export | 1672.73
5:00 | 189 | 46 | 558 | 184 | 1730 | 532
6:00 | 189 | 49 | 524 | 168 | 1652 | 534 |  | Import | 0
7:00 | 189 | 48 | 506 | 110 | 1688 | 530
8:00 | 155 | 14 | 518 | 136 | 1596 | 491 | Sirajganj-Sreepur Ckt-1 | Export | 3057000
9:00 | 204 | 44 | 524 | 168 | 1730 | 600
10:00 | 196 | 37 | 576 | 170 | 1838 | 602 |  | Import | 0
11:00 | 189 | 33 | 532 | 122 | 1848 | 606
12:00 | 194 | 48 | 480 | 122 | 1780 | 602 | Sirajganj-Sreepur Ckt-2 | Export | 3066000
13:00 | 174 | 30 | 480 | 124 | 1746 | 564
14:00 | 165 | 35 | 488 | 146 | 1700 | 580 |  | Import | 0
15:00 | 170 | 38 | 534 | 176 | 1772 | 622
16:00 | 162 | 34 | 492 | 148 | 1596 | 572 | Gopalganj-Aminbazar Ckt-1 | Export | 20770000
17:00 | 166 | 32 | 516 | 150 | 1640 | 574
18:00 | 158 | 26 | 478 | 134 | 1476 | 520 |  | Import | 0
18:30 | 179 | 27 | 542 | 144 | 1660 | 556
19:00 | 179 | 32 | 536 | 168 | 1734 | 558 | Gopalganj-Aminbazar Ckt-2 | Export | 20810000
19:30 | 170 | 28 | 484 | 144 | 1854 | 500
20:00 | 154 | 22 | 452 | 132 | 1852 | 478 |  | Import | 0
21:00 | 156 | 26 | 480 | 170 | 1882 | 492
22:00 | 152 | 22 | 478 | 156 | 1852 | 466 |  | Total Export | 51854709.09
23:00 | 166 | 23 | 516 | 150 | 1912 | 468 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 09-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 378 | 18:00 | 360 | 15:00 | Madunaghat | 396 | 19:00 | 384 | 12:00
Amtali | 410 | 18:30 | 401 | 00:00 | Meghnaghat | 380 | 18:00 | 362 | 13:00
Ashuganj | 404 | 8:00 | 388 | 1200 | Payra | 411 | 18:00 | 405 | 00:00
Bhulta | 395 | 08:00 | 378 | 12:00 | Rahanpur | 403 | 09:00 | 385 | 21:00
Bibiana | 393 | 08:00 | 384 | 00:00 | Rampal | 398 | 18:30 | 382 | 13:00
BIPTC | 401 | 08:00 | 390 | 14:00
Bogura | 387 | 09:00 | 365 | 21:00
Gopalganj | 393 | 18:00 | 375 | 13:00
Kaliakoir | 370 | 18:00 | 352 | 00:00
Korerhat | 396 | 18:30 | 378 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 18:00 | 212 | 13:00 | Jhenaidah | 226 | 18:30 | 211 | 13:00
AKSML | 231 | 18:00 | 219 | 12:00 | Kachua | 231 | 18:00 | 215 | 10:00
Aminbazar | 227 | 18:00 | 213 | 15:00 | Kaliakoir | 227 | 18:00 | 214 | 00:00
Ashuganj | 226 | 08:00 | 218 | 00:00 | Keranigonj | 229 | 04:00 | 211 | 13:00
Ashuganj-400 | 226 | 08:00 | 218 | 00:00 | Khulna(S) | 226 | 18:30 | 212 | 13:00
Baghabari | 232 | 08:00 | 223 | 21:00 | Korerhat | 228 | 18:00 | 215 | 11:00
Barapukuria | 222 | 09:00 | 202 | 21:00 | Madunaghat | 231 | 18:00 | 222 | 11:00
Barapukuria-230 | 222 | 09:00 | 202 | N/A | Madunaghat-400 | 232 | 19:00 | 224 | 11:00
Barishal | 229 | 17:00 | 222 | 00:00 | Maniknagar | 226 | 07:00 | 212 | 12:00
Bheramara | 234 | 06:00 | 222 | 13:00 | Meghnaghat | 231 | 07:00 | 222 | 14:00
Bhulta | 227 | 08:00 | 214 | 13:00 | Meghnaghat-400 | 229 | 08:00 | 215 | 13:00
Bibiana | 230 | 18:30 | 223 | 00:00 | Mirsorai | 229 | 18:00 | 219 | 12:00
BIPTC | 236 | 05:00 | 222 | 13:00 | Naogaon | 217 | 09:00 | 200 | 22:00
Bogura | 240 | 09:00 | 225 | 21:00 | Purbasadipur | 220 | 03:00 | 198 | 21:00
Bogura-400 | 240 | 09:00 | 225 | 21:00 | Rajshahi | 233 | 18:30 | 218 | 13:00
Borhanuddin | 231 | 17:00 | 226 | 00:00 | Rampal | 229 | 23:00 | 213 | 13:00
BSRM | 227 | 18:00 | 215 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 230 | 18:00 | 215 | 13:00 | Rampura | 227 | 08:00 | 211 | 13:00
Cumilla(N) | 227 | 18:00 | 216 | 00:00 | Shikalbaha | 231 | 18:00 | 222 | 10:00
Faridpur | 231 | 18:00 | 216 | 00:00 | Shyampur | 226 | 18:30 | 213 | 13:00
Fenchuganj | 233 | 18:00 | 225 | 00:00 | Siddhirganj | 228 | 07:00 | 215 | 14:00
Feni | 228 | 18:00 | 214 | 12:00 | Sirajgonj | 237 | 06:00 | 230 | 21:00
Ghorashal | 230 | 04:00 | 220 | 10:00 | Sreepur | 224 | 08:00 | 213 | 21:00
Ghorashal-230 | 218 | 08:00 | 200 | 00:00 | Tongi | 217 | 07:00 | 201 | 00:00
Gopalganj | 230 | 18:00 | 219 | 00:00
GPH | 233 | 01:00 | 218 | 12:00
Haripur | 227 | 08:00 | 214 | 13:00
Hasnabad | 226 | 18:00 | 212 | 13:00
Hathazari | 230 | 18:00 | 219 | 10:00
Ishurdi | 235 | 05:00 | 223 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 08:00 | 126 | 13:00 | Madunaghat | 134 | 18:00 | 128 | 10:00
Agargaon | 133 | 08:00 | 124 | 13:00 | Magura | 135 | 18:30 | 122 | 13:00
Agrabad | 131 | 18:00 | 124 | 12:00 | Mahasthangarh | 136 | 04:00 | 123 | 21:00
AKS | 130 | 18:30 | 124 | 10:00 | Maijdee | 130 | 18:00 | 119 | 11:00
Aminbazar | 127 | 18:00 | 120 | 10:00 | Manikganj | 127 | 08:00 | 119 | 00:00
Amnura | 136 | 18:30 | 125 | 13:00 | Maniknagar | 133 | 08:00 | 122 | 13:00
Ashuganj | 135 | 08:00 | 128 | 00:00 | Matarbari | 118 | 18:30 | 108 | 19:00
Ashuganj-230 | 135 | 08:00 | 128 | 00:00 | Matuail | 132 | 18:00 | 123 | 12:00
Bagerhat | 130 | 23:00 | 118 | 00:00 | Metrorail_Motijheel | 133 | 08:00 | 122 | 13:00
Bajitpur | 127 | 12:00 | 119 | 02:00 | Metrorail_Uttara | 131 | 18:00 | 118 | 11:00
Bakerganj | 131 | 17:00 | 126 | 00:00 | Millgate | 132 | 18:00 | 122 | 00:00
Bakulia | 133 | 18:30 | 125 | 10:00 | Mirpur | 128 | 18:00 | 118 | 11:00
Banani | 136 | 05:00 | 125 | 13:00 | Mirzapur | 127 | 10:00 | 120 | 00:00
Bangabhaban | 132 | 04:00 | 122 | 12:00 | Mithapukur | 133 | 09:00 | 120 | 21:00
Barapukuria | 134 | 04:00 | 120 | 21:00 | MI_Cement | 127 | 06:00 | 117.2 | 13:00
Barguna | 131 | 18:30 | 125 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 08:00 | 125 | 13:00 | Mogbazar | 137 | 08:00 | 127 | 13:00
Barishal-230 | 132 | 18:30 | 125 | 13:00 | Mongla | 130 | 23:00 | 118 | 14:00
Baroaulia | 132 | 18:00 | 127 | 12:00 | Motijheel | 132 | 04:00 | 122 | 12:00
Baroirhat | 132 | 18:00 | 124 | 11:00 | Muktagacha | 128 | 12:00 | 114 | 00:00
Bashundhara | 137 | 06:00 | 121 | 00:00 | Munshiganj | 130 | 18:00 | 121 | 13:00
BashundharaCement | 131 | 18:00 | 123 | 12:00 | Muradnagar | 130 | 17:00 | 120 | 00:00
Beanibazar | 126 | 08:00 | 121 | 00:00 | Mymensingh | 129 | 10:00 | 109 | 21:00
Benapole | 131 | 18:30 | 116 | 14:00 | Nabinagar | 130 | 18:00 | 118 | 00:00
Bhaluka | 130 | 11:00 | 119 | 01:00 | Naogaon | 136 | 09:00 | 120 | 21:00
Bhandaria | 129 | 00:00 | 118 | 14:00 | Narail | 136 | 18:30 | 122 | 13:00
Bhangura | 134 | 09:00 | 127 | 21:00 | Narinda | 133 | 08:00 | 122 | 13:00
Bheramara | 136 | 06:00 | 130 | 13:00 | Narshingdi | 130 | 09:00 | 119 | 00:00
Bheramara(GK) | 136 | 09:00 | 130 | 13:00 | Natore | 134 | 05:00 | 126 | 21:00
Bhulta | 128 | 07:00 | 120 | 12:00 | Nawabganj | 136 | 18:00 | 126 | 13:00
Bog-Sherpur | 137 | 09:00 | 127 | 21:00 | Netrakona | 124 | 12:00 | 107 | 21:00
Bogura | 138 | 09:00 | 128 | 21:00 | New | 133 | 18:00 | 123 | 00:00
Bogura-230 | 138 | 09:00 | 128 | 21:00 | Niamatpur | 132 | 09:00 | 124 | 21:00
Brahmanbaria | 130 | 09:00 | 120 | 00:00 | Noapara | 133 | 18:30 | 121 | 13:00
Cantonment | 133 | 18:00 | 123 | 13:00 | Pabna | 134 | 07:00 | 127 | 01:00
Chandina | 132 | 17:00 | 123 | 12:00 | Palashbari | 131 | 05:00 | 117 | 21:00
Chandpur | 133 | 18:00 | 121 | 04:00 | Panchagarh | 139 | 01:00 | 124 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 18:00 | 128 | 11:00 | Patiya | 131 | 18:30 | 124 | 11:00
Chapai | 132 | 06:00 | 127 | 13:00 | Patuakhali | 131 | 09:00 | 125 | 13:00
Charsaidpur | 131 | 18:00 | 122 | 13:00 | Payra | 134 | 09:00 | 131 | 00:00
Chauddagram | 132 | 18:00 | 122 | 11:00 | PHP | 132 | 18:00 | 124 | 11:00
Chhatak | 125 | 05:00 | 117 | 00:00 | Postogola | 130 | 18:00 | 121 | 12:00
Chowmuhani | 131 | 18:00 | 120 | 10:00 | Pubail | 133 | 07:00 | 120 | 12:00
Chuadanga | 134 | 18:30 | 120 | 13:00 | Purbachal | 136 | 05:00 | 125 | 13:00
Coxsbazar | 120 | 08:00 | 110 | 21:00 | Purbasadipur | 133 | 03:00 | 120 | 21:00
Cumilla(N) | 131 | 18:00 | 124 | 00:00 | Rahanpur | 134 | 05:00 | 128 | 21:00
Cumilla(S) | 133 | 18:00 | 123 | 12:00 | Rahanpur-400 | 135 | 09:00 | 128 | 21:00
Daganbhuiyan | 132 | 18:00 | 122 | 04:00 | Rahim | 132 | 18:00 | 123 | 13:00
Daudkandi | 130 | 18:00 | 117 | 12:00 | Rajbari | 133 | 18:00 | 120 | 00:00
DhakaUniversity | 137 | 07:00 | 126 | 12:00 | Rajendrapur | 130 | 08:00 | 121 | 00:00
Dhamrai | 129 | 17:00 | 120 | 00:00 | Rajshahi | 132 | 09:00 | 123 | 13:00
Dhanmondi | 136.7 | 08:00 | 126 | 12:00 | Rajshahi-230 | 134 | 18:30 | 125 | 13:00
Dohazari | 125 | 00:00 | 120 | 13:00 | Ramganj | 131 | 18:00 | 118 | 04:00
Faridpur | 133 | 18:30 | 124 | 00:00 | Rampur | 131 | 18:30 | 126 | 10:00
Fatullah | 131 | 18:00 | 118 | 13:00 | Rampura | 137 | 08:00 | 125 | 13:00
Fenchuganj | 132 | 08:00 | 127 | 00:00 | Rangamati | 133 | 18:30 | 127 | 11:00
Feni | 130 | 18:00 | 124 | 05:00 | Rangpur | 131 | 09:00 | 118 | 21:00
Feni-230 | 132 | 18:00 | 123 | 11:00 | Ruppur | 136 | 08:00 | 130 | 13:00
Ghatail | 126 | 12:00 | 116 | 00:00 | Saidpur | 133 | 1:00 | 125 | 22:00
Ghorashal | 134 | 22:00 | 123 | 00:00 | Santhia | 135 | 08:00 | 128 | 22:00
Goalpara | 136 | 18:30 | 124 | 13:00 | Satkhira | 129 | 18:30 | 117 | 13:00
Gollamari | 135 | 18:30 | 123 | 13:00 | Satmasjid | 133 | 18:30 | 123 | 13:00
Gopalganj | 135 | 18:30 | 123 | 13:00 | Savar | 127 | 18:00 | 118 | 12:00
Gopalganj-400 | 134 | 18:00 | 126 | 13:00 | SevenRings | 133 | 08:00 | 120 | 00:00
Gulshan | 136 | 05:00 | 126 | 12:00 | ShahCement | 131 | 18:00 | 122 | 13:00
Halishahar | 132 | 18:30 | 125 | 10:00 | Shahjadpur | 135 | 04:00 | 132 | 00:00
Haripur | 132 | 08:00 | 124 | 12:00 | Shahjibazar | 133 | 17:00 | 122 | 00:00
HaripurSBU | 132 | 19:30 | 124 | 12:00 | Shahmirpur | 131 | 00:00 | 126 | 10:00
Hasnabad | 129 | 08:00 | 121 | 12:00 | Shariatpur | 135 | 18:30 | 123 | 00:00
Hathazari | 134 | 18:00 | 127 | 12:00 | Sherpur | 129 | 12:00 | 113 | 13:00
Hatirjheel | 137 | 06:00 | 126 | 12:00 | Shikalbaha | 122 | 18:00 | 115 | 11:00
Ishurdi | 137 | 06:00 | 131 | 13:00 | Shikalbaha-230 | 133 | 18:00 | 127 | 11:00
Jaldhaka | 130 | 09:00 | 116 | 21:00 | Shitalakhya | 127 | 06:00 | 117.4 | 13:00
Jamalpur | 129 | 10:00 | 115 | 00:00 | Sholosohor | 132 | 18:00 | 125 | 11:00
Jashore | 131 | 05:00 | 119 | 14:00 | Shomvuganj | 126 | 12:00 | 112 | 21:00
Jhenaidah | 137 | 18:30 | 125 | 14:00 | Shyampur | 138 | 05:00 | 123 | 00:00
Jhenaidah-230 | 137 | 19:00 | 125 | 13:00 | Shyampur-230 | 136 | 18:30 | 126 | 13:00
Joydebpur | 134 | 08:00 | 119 | 00:00 | Siddhirganj | 132 | 18:30 | 124 | 12:00
Joypurhat | 135 | 04:00 | 122 | 21:00 | Sirajganj | 132 | 05:00 | 124 | 21:00
Juldah | 131 | 18:00 | 125 | 10:00 | Sonargaon | 130 | 18:00 | 120 | 13:00
Kabirpur | 131 | 08:00 | 119 | 00:00 | Sreemongol | 130 | 14:00 | 122 | 00:00
Kachua | 132 | 18:00 | 122 | 10:00 | Sreepur | 132 | 08:00 | 123 | 21:00
Kaliakoir | 135 | 18:00 | 125 | 00:00 | Srinagar | 136 | 18:00 | 126 | 13:00
Kaliganj | 136 | 18:30 | 124 | 13:00 | SSM | 136 | 18:00 | 130 | 10:00
Kallyanpur | 129 | 17:00 | 118 | 13:00 | Sunamganj | 124 | 05:00 | 116 | 00:00
Kalurghat | 134 | 18:00 | 128 | 10:00 | Sylhet | 127 | 06:00 | 122 | 00:00
Kamrangirchar | 136 | 18:00 | 117 | 12:00 | Sylhet-132 | 127 | 07:00 | 123 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 126 | 10:00 | 116 | 00:00
Kasba | 130 | 18:00 | 118 | 00:00 | Taraganj | 132 | 09:00 | 119 | 21:00
Kazla | 131 | 05:00 | 122 | 13:00 | Tasnim | 131 | 18:00 | 120 | 13:00
Keranigonj | 136 | 08:00 | 127 | 13:00 | Thakurgaon | 138 | 01:00 | 123 | 21:00
Khagrachori | 133 | 18:00 | 126 | 11:00 | TK | 133 | 18:00 | 127 | 11:00
Khulna | 133 | 08:00 | 123 | 13:00 | Tongi | 133 | 07:00 | 124 | 00:00
Khulna(S) | 135 | 18:30 | 125 | 13:00 | Ullahpara | 134 | 09:00 | 126 | 21:00
Khulshi | 131 | 18:30 | 123 | 12:00 | Ullon | 136 | 06:00 | 126 | 12:00
Kishoreganj | 129 | 12:00 | 115 | 21:00 | Uttara | 131 | 18:30 | 117 | 13:00
Kodda | 131 | 18:00 | 120 | 14:00 | UttaraNew | 131 | 18:00 | 118 | 11:00
Korerhat | 133 | 18:00 | 126 | 11:00 | Zigatola | 136 | 18:00 | 127 | 13:00
KSRM | 133 | 18:00 | 126 | 12:00
Kulaura | 131 | 08:00 | 126 | 00:00
Kurigram | 133 | 04:00 | 114 | 21:00
Kushtia | 134 | 06:00 | 127 | 13:00
Laksam | 132 | 18:00 | 121 | 11:00
Lakshmipur | 129 | 18:00 | 119 | 04:00
Lalbag | 136 | 18:00 | 126 | 13:00
Lalmonirhat | 128 | 03:00 | 118 | 21:00
Madanganj | 131 | 18:00 | 123 | 12:00
Madaripur | 135 | 18:30 | 125 | 13:00
Madartek | 136 | 06:00 | 125 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division