## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-10-2025 | during | 22-10-2025 | during | 22-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 403 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0.01 | 0.01 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 321 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 52.8 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 44 | 120 | 149.36 | 149.36 | 45 | 140 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 19 | 24 | 24 | 24 | 24 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 81 | 81 | 300 | 300 | 65 | 65 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 21 | 72 | 149 | 149 | 17 | 17 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 144 | 162 | 162 | 17 | 17 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 320 | 330 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 142 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1748 | 2287.8 | 5829.4 | 5795.4 | 3914.46 | 4084.46
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 8 | 25.5 | 25.5 | 17 | 17 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 218 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 159 | 158 | 154 | 154 | 154 | 154 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 22 | 68 | 40 | 70 | 40 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 25 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 7 | 43 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.37 | 0 | 3.42 | 0 | 3.42 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 32 | 32 | 300 | 300 | 16 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 17 | 49 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 100 | 89 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 160 | 159.86 | 159.86 | 17 | 159 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1182 | 1190 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 1 | 0 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2438.37 | 2755 | 3582.14 | 3599.72 | 2834.78 | 3028.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 320 | 343 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 408 | 360 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 37 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 37 | 41 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 108 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 93 | 123 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 42 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 100 | 163 | 163 | 105 | 105 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 180 | 177 | 200 | 200 | 180 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 80 | 86 | 160 | 160 | 100 | 100 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 38 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 105 | 109 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 90 | 115 | 115 | 16 | 16 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 45 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1556 | 1729 | 2284.05 | 2224.05 | 1903.05 | 1852.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-10-2025 | during | 22-10-2025 | during | 22-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 72 | 72 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 47 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 69 | 67 | 67 | 67 | 67 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.68 | 0 | 48.2 | 0 | 48.2 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 261.68 | 211 | 399.5 | 349 | 346 | 295.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 66 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 163 | 160 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 10 | 9 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 312 | 312 | 325 | 325 | 325 | 325 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1159 | 1144 | 1218 | 1218 | 1196 | 1196
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 930 | 930 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 39 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 46 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 347 | 329 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 91 | 0 | 84 | 0 | 84 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 940 | 1131 | 0 | 0 | 1096 | 1096 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2346 | 2513 | 2404 | 2320 | 2739 | 2655
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 350 | 513 | 0 | 0 | 0 | 0 | On Test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 19 | 110 | 110 | 16 | 32 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 900 | 1121 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 27 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 199 | 273 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1779.65 | 2283 | 2147 | 2146 | 1920 | 1935
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 61.61 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 41 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 197 | 190 | 214 | 214 | 193 | 193 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 409 | 401 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 94 | 94 | 94 | 94 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 102 | 113 | 113 | 35 | 95 | Fuel shortage as BPDB payment not done in time
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.83 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1021 | 1470.46 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 67.12 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 113 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1874.56 | 2401.46 | 3179.47 | 3012.87 | 2929.09 | 2822.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.7 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 198 | 0 | 193.33 | 0 | 193.33 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 241.7 | 222 | 477.33 | 248 | 457.33 | 228
System Total |  |  |  |  | 28823.2 | 28364.092 | 13404.96 | 15546.26 | 21520.89 | 20913.04 | 18239.71 | 18096.86
Forecast Scenario (22-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14870 |  | 0 |  | 14870
|  |  |  | 1:00 | 14540 |  | 0 |  | 14540
|  |  |  | 2:00 | 14200 |  | 0 |  | 14200
|  |  |  | 3:00 | 13500 |  | 0 |  | 13500
|  |  |  | 4:00 | 13150 |  | 0 |  | 13150
|  |  |  | 5:00 | 12700 |  | 0 |  | 12700
|  |  |  | 6:00 | 12410 |  | 0 |  | 12410
|  |  |  | 7:00 | 12530 |  | 0 |  | 12530
|  |  |  | 8:00 | 12690 |  | 0 |  | 12690
|  |  |  | 9:00 | 12800 |  | 0 |  | 12800
|  |  |  | 10:00 | 12930 |  | 0 |  | 12930
|  |  |  | 11:00 | 13290 |  | 0 |  | 13290
|  |  |  | 12:00 | 14000 |  | 0 |  | 14000
|  |  |  | 13:00 | 14280 |  | 0 |  | 14280
|  |  |  | 14:00 | 14250 |  | 0 |  | 14250
|  |  |  | 15:00 | 14250 |  | 0 |  | 14250
|  |  |  | 16:00 | 14100 |  | 0 |  | 14100
|  |  |  | 17:00 | 13850 |  | 0 |  | 13850
|  |  |  | 18:00 | 15060 |  | 0 |  | 15060
|  |  |  | 18:30 | 15500 |  | 0 |  | 15500
|  |  |  | 19:00 | 15880 |  | 0 |  | 15880
|  |  |  | 19:30 | 15720 |  | 0 |  | 15720
|  |  |  | 20:00 | 15670 |  | 0 |  | 15670
|  |  |  | 21:00 | 15540 |  | 0 |  | 15540
|  |  |  | 22:00 | 15400 |  | 0 |  | 15400
|  |  |  | 23:00 | 15200 |  | 0 |  | 15200
Probable Maximum Temperature: |  |  | 34.50°C
Probable Maximum Demand at Day Peak: |  |  | 14000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15880.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15880.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 337.09 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:54 hrs on 22-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-10-2025 | [28 empty] | Date: | 21-10-2025 | [28 empty] | Date: | 21-10-2025 | [28 empty] | Date: | 21-10-2025 | [28 empty] | Date: | 21-10-2025 | [14 empty] | Date: | 21-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [14 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 17 | 17 | 17 | 47 | 97 | 55 | 0 | 17 | 0 | 300 | 0 | 330 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 0 | 97 | 16 | 98 | 0 | 0 | 50 | 53 | 54.36 | 0 | 0 | 0 | 221 | 96 | 32 | 650 | 17 | 0 | 0 | 17 | 0 | 150 | 0 | 0 | 0 | 1160 | 0 | 51 | 132 | 0 | 415 | 320 | 0 | 43 | 0 | 38 | 0 | 102 | 163 | 0 | 19 | 105 | 90 | 43 | 0 | 35 | 320 | 0 | 312 | 0 | 67 | 158 | 10 | 0 | 81 | 30 | 0 | 16 | 161 | 17 | 69 | 48 | 71 | 0 | 0 | 0 | 7325.36 | 903 | 317 | 0 | 32 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 0 | 1477 | 0 | 16 | 0 | 35 | 95 | 0 | 93 | 23 | 52.2 | 0 | 0 | 25 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 216 | 110 | 180 | 0 | 501 | 1050 | 17 | 7128.2 | 14453.56 | 105.87
01:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 17 | 17 | 47 | 65 | 55 | 0 | 17 | 0 | 300 | 0 | 330 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 0 | 96 | 16 | 98 | 0 | 0 | 50 | 53 | 54.36 | 0 | 0 | 0 | 220 | 0 | 33 | 650 | 17 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1195 | 0 | 51 | 130 | 0 | 415 | 320 | 0 | 42 | 0 | 38 | 0 | 102 | 170 | 0 | 19 | 102 | 94 | 43 | 0 | 35 | 320 | 0 | 312 | 0 | 67 | 159 | 8 | 0 | 81 | 30 | 0 | 16 | 161 | 17 | 69 | 48 | 87 | 0 | 0 | 0 | 7228.36 | 903 | 317 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 1477.14 | 0 | 16 | 0 | 35 | 35 | 0 | 0 | 23 | 52.2 | 0 | 0 | 25 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 115 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 217 | 110 | 180 | 0 | 450 | 1044 | 23 | 6914.34 | 14142.7 | 105.85
02:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 17 | 17 | 47 | 65 | 15 | 0 | 17 | 0 | 300 | 0 | 310 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 0 | 86 | 16 | 97 | 0 | 0 | 50 | 53 | 17 | 0 | 0 | 0 | 219 | 0 | 32 | 650 | 4 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1165 | 0 | 51 | 125 | 0 | 415 | 320 | 0 | 43 | 0 | 35 | 0 | 103 | 171 | 0 | 19 | 68 | 94 | 25 | 0 | 35 | 305 | 0 | 312 | 0 | 67 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 161 | 17 | 69 | 48 | 106 | 0 | 0 | 2 | 7019 | 902 | 317 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 0 | 1477.98 | 0 | 41 | 0 | 35 | 35 | 0 | 0 | 23 | 25 | 0 | 0 | 25 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 110 | 220 | 0 | 403 | 1032 | 17 | 6809.98 | 13828.98 | 105.83
03:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 17 | 47 | 65 | 15 | 0 | 17 | 0 | 300 | 0 | 310 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 21.4 | 22 | 0 | 0 | 82 | 16 | 42 | 0 | 0 | 17 | 38 | 17 | 0 | 0 | 0 | 218 | 0 | 40 | 650 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1195 | 0 | 51 | 60 | 0 | 415 | 320 | 0 | 43 | 0 | 35 | 0 | 103 | 171 | 0 | 19 | 15 | 82 | 8 | 0 | 35 | 300 | 0 | 312 | 0 | 67 | 141 | 8 | 0 | 81 | 30 | 0 | 16 | 161 | 17 | 69 | 48 | 105 | 0 | 0 | 6 | 6776.4 | 903 | 322 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 0 | 1338.97 | 0 | 41 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 35 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 110 | 220 | 0 | 403 | 1034 | 0 | 6443.97 | 13220.37 | 105.81
04:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 17 | 15 | 65 | 0 | 0 | 17 | 0 | 300 | 0 | 305 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 21.4 | 22 | 0 | 0 | 45 | 16 | 42 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 218 | 0 | 40 | 650 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1190 | 0 | 51 | 60 | 0 | 415 | 320 | 0 | 43 | 0 | 35 | 0 | 103 | 179 | 0 | 19 | 2 | 86 | 0 | 0 | 35 | 310 | 0 | 312 | 0 | 67 | 140 | 8 | 0 | 81 | 30 | 0 | 16 | 161 | 17 | 69 | 47 | 105 | 0 | 0 | 6 | 6647.4 | 903 | 330 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 1211.21 | 0 | 41 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 110 | 220 | 0 | 402 | 1031 | 0 | 6244.21 | 12891.61 | 105.79
05:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 17 | 15 | 15 | 0 | 0 | 17 | 0 | 300 | 0 | 315 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 21.4 | 22 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 41 | 650 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1195 | 0 | 51 | 20 | 0 | 415 | 320 | 0 | 43 | 0 | 32 | 0 | 104 | 100 | 0 | 19 | 0 | 86 | 0 | 0 | 35 | 305 | 0 | 312 | 0 | 67 | 144 | 8 | 0 | 78 | 30 | 0 | 16 | 161 | 17 | 68 | 48 | 105 | 0 | 0 | 6 | 6386.4 | 903 | 332 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 1183.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 403 | 1072 | 0 | 6070.83 | 12457.23 | 105.77
06:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 17 | 15 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 310 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 21.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 219 | 0 | 42 | 650 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1135 | 0 | 51 | 0 | 0 | 415 | 320 | 0 | 43 | 0 | 32 | 0 | 104 | 96 | 0 | 19 | 0 | 72 | 0 | 0 | 35 | 300 | 0 | 316 | 0 | 67 | 142 | 8 | 0 | 78 | 30 | 0 | 16 | 161 | 17 | 69 | 48 | 100 | 0 | 0 | 6 | 6219.41 | 903 | 333 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 1165.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 110 | 220 | 0 | 361 | 1089 | 0 | 5958.82 | 12178.23 | 105.75
07:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 17 | 47 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 335 | 0 | 0 | 250 | 0 | 0 | 6 | 17 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63 | 220 | 0 | 37 | 650 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1198 | 5 | 51 | 0 | 0 | 415 | 320 | 0 | 43 | 0 | 38 | 0 | 104 | 96 | 0 | 19 | 0 | 70 | 0 | 15 | 36 | 310 | 0 | 316 | 0 | 67 | 152 | 8 | 0 | 79 | 30 | 0 | 16 | 161 | 17 | 69 | 48 | 87 | 0 | 4.97 | 6 | 6348.6 | 903 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 1011 | 0 | 1076.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.37 | 15 | 0 | 0 | 11.9 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.01 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.9 | 3 | 0.07 | 0 | 198 | 110 | 220 | 0 | 358 | 1088 | 0 | 5990.4 | 12339 | 105.73
08:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 17 | 46 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 335 | 0 | 0 | 250 | 0 | 0 | 16 | 35 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.56 | 220 | 0 | 8 | 650 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1180 | 11 | 51 | 0 | 0 | 418 | 320 | 0 | 43 | 0 | 38 | 0 | 102 | 107 | 0 | 19 | 0 | 72 | 0 | 38 | 35 | 310 | 0 | 316 | 0 | 67 | 150 | 8 | 0 | 79 | 30 | 0 | 16 | 162 | 17 | 69 | 48 | 87 | 1 | 21.4 | 6 | 6388.96 | 910 | 349 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36 | 962 | 0 | 1032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.38 | 46 | 0 | 0 | 31.74 | 175 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 2.73 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 2.6 | 92 | 0.22 | 0 | 191 | 110 | 220 | 0 | 359 | 1050 | 0 | 6052.67 | 12441.63 | 105.72
09:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 17 | 17 | 46 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 340 | 0 | 0 | 250 | 0 | 0 | 25 | 35 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.48 | 221 | 0 | 6 | 650 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1195 | 15 | 51 | 0 | 0 | 416 | 320 | 0 | 43 | 0 | 38 | 3 | 102 | 105 | 0 | 19 | 0 | 73 | 0 | 54 | 36 | 305 | 0 | 316 | 0 | 67 | 150 | 10 | 0 | 81 | 30 | 0 | 16 | 162 | 17 | 69 | 48 | 81 | 2 | 35.34 | 6 | 6447.82 | 916 | 347 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 60 | 930 | 0 | 1031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.28 | 75 | 0 | 0 | 49.33 | 183 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 4.18 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 4.4 | 142 | 0.4 | 0 | 200 | 110 | 220 | 0 | 358 | 980 | 0 | 6128.59 | 12576.41 | 105.71
10:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 17 | 17 | 46 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 360 | 0 | 17 | 250 | 0 | 0 | 29 | 35 | 19 | 22 | 0 | 0 | 7 | 15 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3.07 | 221 | 0 | 6 | 650 | 17 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1185 | 18 | 43 | 2 | 0 | 409 | 320 | 0 | 42 | 0 | 38 | 17 | 99 | 119 | 0 | 19 | 14 | 70 | 0 | 66 | 35 | 320 | 0 | 312 | 0 | 67 | 156 | 10 | 0 | 81 | 30 | 0 | 16 | 162 | 17 | 69 | 48 | 81 | 2 | 44.12 | 6 | 6595.19 | 916 | 341 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 931 | 0 | 976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.31 | 98 | 0 | 0 | 61.64 | 195 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.24 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 5.7 | 174 | 0.51 | 0 | 200 | 110 | 220 | 0 | 348 | 900 | 0 | 6099.4 | 12694.59 | 105.7
11:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 17 | 44 | 80 | 0 | 5 | 17 | 0 | 300 | 0 | 320 | 0 | 17 | 300 | 0 | 0 | 33 | 35 | 19 | 22 | 0 | 0 | 69 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 3.38 | 221 | 0 | 2 | 650 | 17 | 0 | 0 | 6 | 0 | 153 | 0 | 0 | 0 | 1107 | 20 | 43 | 51 | 0 | 407 | 320 | 0 | 38 | 0 | 34 | 17 | 99 | 167 | 2 | 19 | 95 | 79 | 12 | 46 | 28 | 320 | 0 | 312 | 0 | 67 | 158 | 10 | 0 | 81 | 30 | 0 | 16 | 162 | 17 | 69 | 48 | 72 | 2 | 47.02 | 6 | 6887.4 | 922 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 87 | 917 | 0 | 984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.16 | 112 | 0 | 0 | 65.27 | 192 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.8 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 6.6 | 192 | 0.62 | 0 | 203 | 110 | 220 | 0 | 350 | 900 | 0 | 6167.45 | 13054.85 | 105.69
12:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 21 | 44 | 81 | 0 | 17 | 17 | 0 | 300 | 0 | 320 | 0 | 35 | 300 | 0 | 0 | 33 | 35 | 19 | 22 | 0 | 0 | 100 | 32 | 7 | 0 | 0 | 0 | 22 | 17 | 0 | 0 | 3.37 | 221 | 0 | 2 | 650 | 17 | 0 | 0 | 8 | 0 | 159 | 0 | 0 | 0 | 1182 | 18 | 43 | 93 | 0 | 408 | 320 | 0 | 37 | 0 | 36 | 17 | 98 | 180 | 8 | 19 | 105 | 80 | 38 | 45 | 29 | 325 | 0 | 312 | 0 | 67 | 156 | 10 | 0 | 80 | 30 | 0 | 16 | 163 | 17 | 69 | 48 | 72 | 2 | 47.68 | 6 | 7163.05 | 930 | 347 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 91 | 940 | 0 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.61 | 113 | 0 | 0 | 67.12 | 197 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 5.83 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 6.7 | 198 | 0.65 | 0 | 199 | 110 | 220 | 0 | 350 | 900 | 0 | 6241.91 | 13404.96 | 105.68
13:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 30 | 44 | 81 | 0 | 30 | 17 | 0 | 300 | 0 | 305 | 0 | 35 | 300 | 0 | 0 | 32 | 35 | 19 | 22 | 0 | 0 | 87 | 32 | 42 | 0 | 0 | 0 | 38 | 17 | 0 | 0 | 3.17 | 220 | 0 | 13 | 650 | 17 | 0 | 0 | 8 | 0 | 158 | 0 | 0 | 0 | 1187 | 4 | 51 | 102 | 0 | 406 | 320 | 0 | 37 | 0 | 36 | 33 | 98 | 179 | 9 | 19 | 102 | 84 | 43 | 59 | 34 | 320 | 0 | 312 | 0 | 66 | 155 | 10 | 0 | 82 | 30 | 0 | 16 | 162 | 17 | 69 | 48 | 72 | 2 | 39.81 | 6 | 7250.98 | 930 | 343 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 84 | 1031 | 0 | 1113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.24 | 106 | 0 | 0 | 63.41 | 183 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 5.53 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 6.1 | 183 | 0.16 | 0 | 198 | 110 | 220 | 0 | 350 | 920 | 0 | 6420.44 | 13671.42 | 105.67
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 35 | 44 | 81 | 0 | 35 | 17 | 0 | 300 | 0 | 305 | 0 | 35 | 300 | 0 | 0 | 28 | 35 | 19 | 21 | 0 | 0 | 85 | 32 | 43 | 0 | 0 | 0 | 46 | 17 | 0 | 0 | 2.62 | 220 | 0 | 3 | 650 | 17 | 0 | 0 | 8 | 0 | 158 | 0 | 0 | 0 | 1191 | 16 | 51 | 105 | 0 | 404 | 320 | 0 | 40 | 0 | 33 | 44 | 97 | 178 | 0 | 19 | 102 | 84 | 34 | 59 | 34 | 315 | 0 | 312 | 0 | 66 | 155 | 10 | 0 | 80 | 30 | 0 | 16 | 163 | 17 | 69 | 48 | 72 | 2 | 37.28 | 6 | 7230.9 | 929 | 341 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 71 | 1047 | 0 | 1172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.68 | 93 | 0 | 0 | 41.2 | 184 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.64 | 0 | 0 | 35 | 30 | 0 | 0 | 0 | 0 | 5.4 | 150 | 0.5 | 0 | 197 | 110 | 220 | 0 | 350 | 940 | 0 | 6425.42 | 13656.32 | 105.66
15:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17.5 | 17 | 35 | 44 | 81 | 0 | 35 | 17 | 0 | 300 | 0 | 320 | 0 | 35 | 300 | 0 | 0 | 20 | 35 | 18 | 21 | 0 | 0 | 86 | 32 | 46 | 0 | 0 | 0 | 50 | 17 | 0 | 0 | 1.84 | 220 | 0 | 2 | 650 | 17 | 0 | 0 | 8 | 0 | 159 | 0 | 0 | 0 | 1201 | 12 | 51 | 105 | 15 | 400 | 333 | 0 | 40 | 0 | 35 | 88 | 97 | 178 | 0 | 19 | 108 | 92 | 34 | 45 | 30 | 320 | 0 | 312 | 0 | 66 | 154 | 10 | 0 | 80 | 30 | 0 | 16 | 163 | 17 | 69 | 48 | 72 | 1 | 29.51 | 6 | 7312.85 | 930 | 333 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 1074 | 0 | 1199.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.97 | 70 | 0 | 0 | 39.52 | 195 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 3.33 | 0 | 0 | 40 | 22 | 0 | 0 | 0 | 0 | 3.9 | 111 | 0.34 | 0 | 203 | 110 | 220 | 0 | 352 | 955 | 0 | 6395.27 | 13708.12 | 105.65
16:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 40 | 17 | 37 | 44 | 81 | 14 | 35 | 17 | 0 | 300 | 0 | 310 | 0 | 35 | 300 | 0 | 0 | 10 | 35 | 18 | 14 | 0 | 0 | 87 | 32 | 44 | 0 | 1 | 0 | 68 | 17 | 0 | 0 | 0.89 | 216 | 0 | 2 | 650 | 17 | 0 | 0 | 8 | 0 | 158 | 0 | 0 | 0 | 1190 | 6 | 51 | 105 | 51 | 405 | 341 | 0 | 41 | 0 | 33 | 89 | 98 | 179 | 0 | 19 | 104 | 94 | 43 | 21 | 34 | 315 | 0 | 312 | 0 | 66 | 154 | 10 | 0 | 80 | 30 | 0 | 18 | 162 | 17 | 69 | 48 | 72 | 1 | 10.96 | 6 | 7334.85 | 930 | 332 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 1055 | 0 | 1214.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.36 | 36 | 0 | 0 | 21.31 | 187 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 1.86 | 0 | 0 | 50 | 10 | 49 | 0 | 0 | 0 | 1.9 | 60 | 0.15 | 0 | 194 | 110 | 220 | 0 | 350 | 951 | 0 | 6250.57 | 13585.42 | 105.64
17:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 48.8 | 17 | 40 | 44 | 81 | 15 | 55 | 105 | 0 | 300 | 0 | 310 | 0 | 35 | 300 | 0 | 0 | 1 | 35 | 19 | 21 | 0 | 0 | 86 | 32 | 42 | 0 | 1 | 0 | 68 | 17 | 0 | 0 | 0.04 | 216 | 0 | 12 | 650 | 53 | 0 | 0 | 8 | 0 | 158 | 0 | 0 | 0 | 1185 | 1 | 51 | 108 | 53 | 345 | 341 | 0 | 41 | 0 | 33 | 89 | 99 | 179 | 0 | 19 | 104 | 82 | 43 | 2 | 34 | 315 | 0 | 312 | 0 | 66 | 151 | 10 | 0 | 82 | 30 | 0 | 16 | 162 | 17 | 69 | 48 | 72 | 0 | 1.88 | 6 | 7390.72 | 929 | 327 | 0 | 11 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 1027 | 0 | 1376.44 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.58 | 6 | 0 | 0 | 2.23 | 172 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0.17 | 0 | 0 | 50 | 2 | 49 | 0 | 0 | 0 | 0.3 | 10 | 0.02 | 0 | 197 | 110 | 180 | 0 | 350 | 908 | 0 | 6112.74 | 13503.46 | 105.63
18:00 | 0 | 48 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 36.2 | 35 | 72 | 121 | 81 | 15 | 55 | 144 | 0 | 300 | 0 | 300 | 0 | 55 | 300 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 0 | 91 | 32 | 37 | 0 | 0 | 15 | 68 | 27 | 0 | 0 | 0 | 218 | 0 | 15 | 650 | 160 | 0 | 0 | 8 | 0 | 158 | 0 | 0 | 0 | 1160 | 0 | 51 | 115 | 103 | 340 | 330 | 0 | 41 | 0 | 37 | 89 | 99 | 181 | 0 | 19 | 91 | 100 | 43 | 0 | 34 | 310 | 0 | 312 | 0 | 66 | 149 | 10 | 0 | 83 | 30 | 0 | 16 | 160 | 17 | 69 | 47 | 72 | 0 | 0 | 6 | 7822.2 | 929 | 318 | 0 | 32 | 25 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1078 | 0 | 1476.13 | 0 | 41 | 0 | 35 | 10 | 0 | 94 | 15 | 8 | 0 | 0 | 25 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 112 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 106 | 180 | 0 | 411 | 955 | 7 | 6725.13 | 14547.33 | 105.62
19:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 52.8 | 35 | 72 | 120 | 81 | 15 | 55 | 144 | 0 | 300 | 0 | 330 | 0 | 55 | 321 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 0 | 89 | 32 | 43 | 0 | 0 | 65 | 68 | 49 | 0 | 0 | 0 | 218 | 0 | 25 | 650 | 160 | 0 | 0 | 8 | 0 | 158 | 0 | 0 | 0 | 1190 | 0 | 51 | 123 | 108 | 360 | 343 | 0 | 41 | 0 | 37 | 90 | 100 | 177 | 0 | 19 | 109 | 86 | 43 | 0 | 42 | 315 | 0 | 312 | 0 | 66 | 153 | 9 | 0 | 83 | 30 | 0 | 16 | 160 | 17 | 69 | 47 | 72 | 0 | 0 | 6 | 8126.8 | 930 | 329 | 0 | 39 | 46 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1131 | 0 | 1470.46 | 0 | 41 | 0 | 35 | 102 | 0 | 94 | 35 | 8 | 0 | 0 | 25 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 273 | 110 | 220 | 0 | 513 | 1121 | 27 | 7419.46 | 15546.26 | 105.62
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 52 | 35 | 72 | 120 | 81 | 15 | 55 | 144 | 0 | 300 | 0 | 315 | 0 | 55 | 321 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 0 | 92 | 16 | 38 | 0 | 0 | 65 | 68 | 54.36 | 0 | 0 | 0 | 218 | 0 | 22 | 650 | 53 | 0 | 0 | 8 | 0 | 158 | 0 | 0 | 0 | 1192 | 0 | 51 | 125 | 108 | 393 | 339 | 0 | 41 | 0 | 37 | 90 | 100 | 187 | 0 | 19 | 108 | 90 | 43 | 0 | 42 | 325 | 0 | 312 | 0 | 66 | 154 | 9 | 0 | 83 | 30 | 0 | 16 | 160 | 17 | 69 | 48 | 72 | 0 | 0 | 0 | 8040.36 | 929 | 324 | 0 | 34 | 60 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1123 | 0 | 1478.6 | 0 | 41 | 0 | 35 | 113 | 0 | 94 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 276 | 110 | 220 | 0 | 453 | 1110 | 27 | 7375.6 | 15415.96
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 49.4 | 35 | 72 | 119 | 81 | 15 | 55 | 144 | 0 | 300 | 0 | 315 | 0 | 55 | 321 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 94 | 16 | 39 | 0 | 0 | 65 | 68 | 54.36 | 0 | 0 | 0 | 220 | 0 | 34 | 650 | 53 | 0 | 0 | 8 | 0 | 155 | 0 | 0 | 0 | 1190 | 0 | 51 | 127 | 100 | 393 | 342 | 0 | 42 | 0 | 37 | 90 | 100 | 182 | 3 | 19 | 98 | 88 | 43 | 0 | 43 | 320 | 0 | 312 | 0 | 66 | 157 | 9 | 0 | 83 | 30 | 0 | 16 | 160 | 17 | 69 | 47 | 72 | 0 | 0 | 0 | 8031.76 | 929 | 324 | 0 | 32 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1132 | 0 | 1472.96 | 0 | 41 | 0 | 35 | 112 | 0 | 94 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 275 | 110 | 220 | 0 | 453 | 1110 | 27 | 7350.96 | 15382.72 | 105.61
21:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 47.3 | 35 | 72 | 119 | 81 | 15 | 55 | 144 | 0 | 300 | 0 | 305 | 0 | 55 | 322 | 0 | 0 | 0 | 142 | 0 | 22 | 0 | 0 | 89 | 16 | 42 | 0 | 0 | 65 | 68 | 54.36 | 0 | 0 | 0 | 220 | 0 | 37 | 650 | 17 | 0 | 0 | 8 | 0 | 154 | 0 | 0 | 0 | 1190 | 0 | 51 | 127 | 63 | 393 | 345 | 0 | 43 | 0 | 37 | 90 | 101 | 180 | 9 | 19 | 96 | 92 | 43 | 0 | 43 | 315 | 0 | 312 | 0 | 67 | 156 | 9 | 0 | 83 | 30 | 0 | 16 | 160 | 17 | 69 | 47 | 72 | 0 | 0 | 0 | 7933.66 | 930 | 325 | 0 | 32 | 53 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1128 | 0 | 1465 | 0 | 41 | 0 | 35 | 113 | 0 | 94 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 274 | 110 | 220 | 0 | 453 | 1108 | 27 | 7324 | 15257.66 | 105.61
22:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 45.4 | 17 | 72 | 119 | 81 | 20 | 35 | 144 | 0 | 300 | 0 | 300 | 0 | 35 | 324 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 0 | 85 | 16 | 44 | 0 | 0 | 65 | 60 | 54.36 | 0 | 0 | 0 | 220 | 0 | 40 | 650 | 17 | 0 | 0 | 8 | 0 | 154 | 0 | 0 | 0 | 1185 | 0 | 51 | 127 | 35 | 386 | 344 | 0 | 42 | 0 | 37 | 90 | 101 | 174 | 9 | 19 | 98 | 98 | 43 | 0 | 43 | 310 | 0 | 312 | 0 | 67 | 151 | 9 | 0 | 83 | 30 | 0 | 16 | 160 | 17 | 69 | 48 | 72 | 0 | 0 | 0 | 7839.76 | 930 | 324 | 0 | 32 | 49 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 0 | 1460 | 0 | 41 | 0 | 35 | 113 | 0 | 94 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 115 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 269 | 110 | 220 | 0 | 453 | 1106 | 27 | 7290 | 15129.76 | 105.61
23:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 43.6 | 17 | 72 | 45 | 81 | 55 | 35 | 144 | 0 | 300 | 0 | 292 | 0 | 35 | 280 | 0 | 0 | 0 | 35 | 21 | 22 | 0 | 0 | 82 | 16 | 44 | 0 | 0 | 66 | 59 | 54.36 | 0 | 0 | 0 | 221 | 0 | 40 | 650 | 17 | 0 | 0 | 8 | 0 | 147 | 0 | 0 | 0 | 1190 | 0 | 51 | 128 | 35 | 393 | 320 | 0 | 40 | 0 | 37 | 89 | 102 | 163 | 0 | 20 | 98 | 98 | 43 | 0 | 43 | 300 | 0 | 312 | 0 | 67 | 138 | 9 | 0 | 83 | 30 | 0 | 16 | 160 | 17 | 69 | 48 | 70 | 0 | 0 | 0 | 7559.96 | 930 | 332 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 1469 | 0 | 41 | 0 | 35 | 113 | 0 | 94 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 273 | 110 | 220 | 0 | 451 | 1095 | 17 | 7166 | 14725.96 | 105.6
Total KWH | 0 | 1342080 | 396960 | 0 | 0 | 0 | 0 | 0 | 9784800 | 0 | 0 | 489960 | 506880 | 905904 | 1371360 | 1424662 | 330250 | 528880 | 1333440 | 0 | 7580000 | 0 | 7655450 | 0 | 529399 | 7005385 | 0 | 0 | 232780 | 1219200 | 469200 | 513000 | 0 | 0 | 1647218 | 446618 | 824640 | 0 | 1920 | 525319 | 902864 | 636723 | 0 | 0 | 23160 | 5257180 | 20100 | 537600 | 15636363.64 | 562036 | 0 | 0 | 140608.8 | 0 | 3641792 | 0 | 0 | 0 | 28445452 | 123930 | 1202172 | 2050763 | 568727 | 9618000 | 8232000 | 0 | 989280 | 0 | 859752 | 1029120 | 2395163 | 3825600 | 52080 | 456180 | 1640460 | 2008320 | 660106 | 455191 | 852320 | 7613500 | 0 | 7866000 | 0 | 1569000 | 3631909 | 256968 | 0 | 1953600 | 712896 | 0 | 383000 | 3347090 | 429840 | 1639200 | 1149600 | 1877760 | 15600 | 318630 | 107520 | 172760461.44 | 22257454 | 8144064 | 0 | 183360 | 213248 | 912000 | 0 | 0 | 0 | 0 | 0 | 602640 | 25301820 | 0 | 30388817 | 0 | 421434 | 0 | 399936 | 861696 | 0 | 617712 | 247160 | 167362 | 441884 | 784430 | 256200 | 0 | 462752 | 4372091 | 0 | 0 | 0 | 0 | 0 | 9240145 | 0 | 40020 | 0 | 0 | 1339781 | 251494 | 1213353 | 0 | 0 | 0 | 44313 | 1351440 | 3748 | 252576 | 5280000 | 2642000 | 5331150 | 0 | 9508140 | 25085090.91 | 198000 | 158817310.91 | 331577772.35

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 21-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13404.96 | MW | 12:00 Hr. | Energy Generated |  |  | 331.5778 |  | MKWHr.
| Day Peak Demand |  |  | 13802.96 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.617 |  | MKWHr.
| Evening Peak Generation |  |  | 15546.26 | MW | 19:00 Hr. | Energy Demand |  |  | 335.1948 |  | MKWHr.
| Evening Peak Demand |  |  | 15681.07 | MW | 19:00 Hr. | Maximum Temperature |  |  | 35.7 |  | °C
| Minimum Generation of the Day |  |  | 12178.23 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 871.1 |  | MMCFD
| Maximum Generation of the Day |  |  | 15546.26 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.5867 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.0078 | 0 | 10.379 | 0 | 0 | 0.23278 | 0 | 0 | 43.6196 | Gas | 120.4497 | Gas | 427097411.35
| Chattogram Zone |  |  | 4.1794 | 44.0818 | 5.7061 | 0 | 5.2572 | 0.14709 | 0 | 0.00192 | 59.3735 | Coal | 109.2569 | Coal | 693631053.209
| Cumilla Zone |  |  | 24.3213 | 0 | 10.1104 | 0 | 0 | 0.45519 | 2.0083 | 0 | 36.8952 | HFO | 35.8935 | HFO | 647005227.762
| Mymensingh Zone |  |  | 1.8778 | 0 | 3.3262 | 0 | 0 | 0.33423 | 0 | 0 | 5.5381 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.334 | Hydro | 5.2572 | Hydro | 525718
| Khulna Zone |  |  | 8.1441 | 25.3018 | 0.39661 | 0 | 0 | 0.60264 | 23.1695 | 0 | 57.6146 | Solar | 5.152 | Solar | 82562062.6
| Barishal Zone |  |  | 7.9732 | 39.8732 | 0.45058 | 0 | 0 | 0.003748 | 0 | 0 | 48.3007 | Import | 55.5666 | Import | 333160989.86
| Rajshahi Zone |  |  | 13.6122 | 0 | 2.9715 | 0 | 0 | 1.7291 | 30.3888 | 0 | 48.7016 | Wind | 0.00192 | Wind | 28243.2
| Rangpur Zone |  |  | 0 | 0 | 2.5531 | 0 | 0 | 1.6472 | 0 | 0 | 4.2004
| Total |  |  | 120.4497 | 109.2569 | 35.8935 | 0 | 5.2572 | 5.152 | 55.5666 | 0.00192 | 331.5778
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 427097411.35 |  | Hydro | 525718
|  |  |  | Coal | 693631053.209 |  | Solar | 82562062.6
|  |  |  | HFO | 647005227.762 |  | Import | 333160989.86
|  |  |  | HSD | 0 |  | Wind | 28243.2
[5 empty] | Total: | 218,40,10,705 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2575 | Peak Hr Flow | 930.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44527090.97 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.3888 | Peak Hr Flow | 1470.46 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2561 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.0083 | Peak Hr Flow | 86.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2644 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.6546 | Peak Hr Flow | 2486.46 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 20 |  | 5525
|  |  |  | Chattogram |  | 0 |  | 1512
|  |  |  | Cumilla |  | 0 |  | 1530
|  |  |  | Mymensingh |  | 99 |  | 1137
|  |  |  | Sylhet |  | 0 |  | 685
|  |  |  | Khulna |  | 0 |  | 1757
|  |  |  | Barishal |  | 0 |  | 469
|  |  |  | Rajshahi |  | 0 |  | 1463
|  |  |  | Rangpur |  | 10 |  | 926
|  |  |  | Total |  | 129 |  | 15004
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:07 | 14:21 | Cumilla(S) 132/33kV S/S Tripura Ckt-1 Scheduled S/D Due to Annual Maintenance
| 08:11 | 17:11 | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to Annual maintence
| 08:13 | 17:10 | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to Annual maintenance
| 08:17 | 16:04 | Gopalganj 132/33kV S/S T2 LT Scheduled S/D Due to Y/M
| 08:18 | 16:03 | Gopalganj 132/33kV S/S T2 HT Scheduled S/D Due to Y/M
| 08:29 | 17:26 | Bogura-Sirajganj 230 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end Due to Annual
Maintenance and from Sirajgonj 230 end Due to Annual Maintenance
| 08:31 | 12:44 | Savar 132/33kV S/S Capacitor Bank-2 Scheduled S/D Due to Annual maintenance
| 08:37 |  | Sathia- Baghabari 132 KV ckt S/D due to OPGW stringing.
| 08:45 | 12:38 | Savar 132/33kV S/S Bus-B Scheduled S/D Due to Annual maintenance
| 08:58 | 16:13 | Saidpur 132/33kV S/S TR-5 (434T) LT Scheduled S/D Due to Annual Maintenance.
| 08:59 | 17:08 | Barishal 230/132kV S/S ATR-2 LT Scheduled S/D Due to Annual maintenance
| 08:59 | 17:09 | Barishal 230/132kV S/S ATR-2 HT Scheduled S/D Due to Annual maintenance
| 09:01 | 17:04 | Tongi 230/132/33kV S/S Tongi-Uttara Ckt Scheduled S/D Due to Annual maintenance
| 09:07 | 14:41 | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to For annual
maintenance.
| 09:18 | 17:23 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual maintenance
| 09:30 | 15:24 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Scheduled S/D Due to For Annual maintenance work
| 09:30 | 15:24 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Scheduled S/D Due to For annual maintenance work
| 09:45 | 13:32 | Hathazari-Raozan 230kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to Annual
Maintenance work
| 09:50 | 17:23 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to by
NLDC
| 10:08 | 14:52 | Tongi 230/132/33kV S/S Tongi-Tongi 80 MW PS Scheduled S/D Due to Annual maintenance 80 MW
ending side.
|  | 11:16 | Dhamrai 132/33kV S/S Transformer-1 LT is restored.
|  | 11:16 | Dhamrai 132/33kV S/S Transformer-1 HT is restored.
| 11:52 |  | Sathia- Baghabari 132 KV ckt ( Up to tower no. 256 including Bera 70 MW PS From
Baghabari end) Synchronized.
| 12:00 |  | Day Peak Gen. 13404 MW
| 12:15 | 16:54 | Aminbazar 400/230/132kV S/S 230 kv Bus 01 Scheduled S/D Due to Annual maintenance
| 13:22 |  | Khulna(S) 230/132kV S/S Rupsha Ckt-1 Tripped showing line Diff(87L) relays.
| 17:10 |  | BIPTC S/S 20DF12 Tripped showing 60/61 relays Due to A dead bird has been noticed inside
the fence area.
| 17:14 |  | Sathia- Baghabari 132 KV ckt (Up to tower no. 256 including Bera 70 MW PS From Baghabari
end) charged from Sathia. 256 No. tower loop jumper is kept open.
|  | 17:54 | Barguna 132/33kV S/S Transformer-1 HT is restored.
|  | 17:55 | Barguna 132/33kV S/S Transformer-1 LT is restored.
| 20:35 | 21:42 | Baroirhat-Hathazari 132 kV Ckt-1 Forced S/D from Baroirhat 132/33kV end Due to Order by
NLDC
| 20:36 | 21:42 | Baroirhat-Hathazari 132 kV Ckt-2 Forced S/D from Baroirhat 132/33kV end Due to Order by
NLDC
| 21:09 | 21:47 | Madunaghat 132/33kV S/S 132kV BUS Forced S/D Due to According to the instructions of
NLDC.
| 22:20 | 23:32 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to Red hot at 5 no feeder source side | [7 empty] | 17.0MW load
|  |  | maintenance by Mpbs. | [7 empty] | interrup.
| 22:20 | 23:32 | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to Red hot at 5 no feeder source side | [7 empty] | 17.0MW load
|  |  | maintenance by Mpbs. | [7 empty] | interrup.
| 22:29 | 23:33 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Forced S/D Due to keranihut feeder 33kv | [7 empty] | 71.0MW load
|  |  | redhot maintanance | [7 empty] | interrup.
| 22:30 | 23:32 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Forced S/D Due to keranihut feeder 33kv | [7 empty] | 71.0MW load
|  |  | redhot maintanance | [7 empty] | interrup.
| 06:00 |  | Minimum Generation is 12327 MW
| 07:20 |  | Barguna 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual Maintenance Work.
| 07:21 |  | Barguna 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual Maintenance Work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 403 | 9784800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7580000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 330250 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 321 | 7005385 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 52.8 | 489960 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 120 | 1371360 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 528880 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 529399 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 469200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 513000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 396960 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 1424662 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 72 | 905904 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1342080 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1333440 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 232780 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 506880 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 330 | 7655450 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1219200 | Engine Problem
Dhaka Area Total |  |  |  |  | 6655.861 | 2287.8 | 43619590
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 140608.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 123930 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 218 | 5257180 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 158 | 3641792 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 68 | 902864 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 525319 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 537600 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 43 | 824640 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23160 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 446618 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 49 | 636723 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 20100 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 89 | 1647218 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 160 | 562036 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1190 | 28445452 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 1920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15636363.64 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2755 | 59373524.44
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 343 | 8232000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 360 | 9618000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 859752 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 41 | 989280 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 108 | 568727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1202172 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 123 | 2050763 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 852320 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2395163 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 177 | 3825600 | -
| Import (Tripura) |  | Import | 0 | 160 | 86 | 2008320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 660106 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 456180 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 109 | 1640460 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 52080 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1029120 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 455191 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1729 | 36895234
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 72 | 1877760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 47 | 1149600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 1639200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 318630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 107520 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 429840 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 211 | 5538150
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 66 | 1569000 | GT3,4 are not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3631909 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 712896 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1953600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3347090 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 383000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 9 | 256968 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7613500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 312 | 7866000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1144 | 27333963
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 930 | 22257454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 39 | 183360 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 46 | 213248 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 329 | 8144064 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 602640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1131 | 25301820 | U1 Partial load due to PA fan outage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2513 | 57614586
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 513 | 9508140 | On Test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 19 | 252576 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2642000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1121 | 25085090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5331150 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 27 | 198000 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 273 | 5280000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3748 | -
Barishal Area Total |  |  |  |  | 2858 | 2283 | 48300704.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 441884 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 41 | 421434 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 247160 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 190 | 4372091 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 401 | 9240145 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 256200 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 167362 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 617712 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 102 | 861696 | Fuel shortage as BPDB payment not done in time
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 399936 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 40020 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1470.46 | 30388817 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 462752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 784430 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2401.46 | 48701639
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1213353 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44313 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1339781 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 251494 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1351440 | -
Rangpur Area Total |  |  |  |  | 950 | 222 | 4200381
Eastern Grid Total |  |  |  |  | 17383.852 | 8126.8 | 172760461.44
Western Grid Total |  |  |  |  | 10980.24 | 7419.46 | 158817310.91
National Grid Total |  |  |  |  | 28364.092 | 15546.26 | 331577772.35
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10270.78 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4604.3 | MW
i) Dhaka area |  |  | 5505.39 |  | MW | i) Khulna area |  |  |  | 1757 | MW
ii) Chattogram area |  |  | 1512.5 |  | MW | ii) Barishal area |  |  |  | 468.7 | MW
iii) Cumilla area |  |  | 1529.89 |  | MW | iii) Rajshahi area |  |  |  | 1462.6 | MW
iv) Mymensingh area |  |  | 1038 |  | MW | iv) Rangpur area |  |  |  | 916 | MW
v) Sylhet area |  |  | 685 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14875.08 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 83 | 19:00 | 133 | Niamatpur | 77 | 21:00
2 | AKSML | 90 | 16:00 | 68 | Ishurdi | 80 | 18:30 | 134 | Noapara | 44 | 18:30
3 | Aftabnagar | 42 | 23:00 | 69 | Jaldhaka | 75 | 18:30 | 135 | PHP | 7 | 03:00
4 | Agargaon | 141 | 13:00 | 70 | Jamalpur | 125 | 07:00 | 136 | Pabna | 102 | 18:00
5 | Agrabad | 106 | 18:30 | 71 | Jashore | 144 | 13:00 | 137 | Palashbari | 122 | 18:00
6 | Amnura | 36 | 20:00 | 72 | Jhenaidah | 133 | 19:00 | 138 | Panchagarh | 60 | 18:00
7 | Ashuganj | 95 | 23:00 | 73 | Joydebpur | 160 | 18:30 | 139 | Patiya | 11.32 | 18:00
8 | BSRM | 196 | 07:00 | 74 | Joypurhat | 60 | 22:00 | 140 | Patuakhali | 71.5 | 22:00
9 | Bagerhat | 80 | 00:00 | 75 | Juldah | 18 | 11:00 | 141 | Payra | 32 | 21:00
10 | Bajitpur | 73 | 22:00 | 76 | KSRM | 45 | 00:00 | 142 | Postogola | 70 | 18:30
11 | Bakulia | 91 | 19:30 | 77 | Kabirpur | 231 | 18:30 | 143 | Purbachal | 23 | 18:00
12 | Banani | 55.4 | 13:00 | 78 | Kachua | 103 | 18:00 | 144 | Purbasadipur | 118 | 19:00
13 | Bangabhaban | 27 | 11:00 | 79 | Kallyanpur | 105 | 00:00 | 145 | Rahanpur | 35 | 21:00
14 | Barapukuria | 58 | 19:30 | 80 | Kalurghat | 52 | 15:00 | 146 | Rahim | 15 | 09:00
15 | Barguna | 22 | 18:30 | 81 | Kamrangirchar | 82 | 18:00 | 147 | Rajbari | 80 | 18:30
16 | Barishal | 117 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 131 | 18:30
17 | Barishal-230 | 100 | 19:30 | 83 | Kasba | 38 | 19:30 | 149 | Rajshahi | 109 | 00:00
18 | Baroaulia | 72 | 11:00 | 84 | Kazla | 102 | 19:30 | 150 | Rajshahi-230 | 89 | 13:00
19 | Baroirhat | 68 | 18:30 | 85 | Keranigonj | 88 | 19:30 | 151 | Ramganj | 120 | 20:00
20 | Bashundhara | 218 | 13:00 | 86 | Khagrachori | 36 | 18:00 | 152 | Rampur | 60 | 23:00
21 | BashundharaCement | 8 | 10:00 | 87 | Khulna | 64 | 12:00 | 153 | Rangamati | 15 | 18:30
22 | Beanibazar | 84 | 18:30 | 88 | Khulshi | 188 | 20:00 | 154 | Rangpur | 139 | 18:30
23 | Benapole | 58 | 18:00 | 89 | Kishoreganj | 124 | 18:30 | 155 | Ruppur | 7.6 | 10:00
24 | Bhaluka | 133 | 21:00 | 90 | Kodda | 278 | 21:00 | 156 | SSM | 14 | 05:00
25 | Bhandaria | 50 | 21:00 | 91 | Kulaura | 53 | 19:00 | 157 | Saidpur | 104 | 18:30
26 | Bhangura | 36 | 20:00 | 92 | Kurigram | 60 | 18:30 | 158 | Satkhira | 125 | 21:00
27 | Bheramara(GK) | 66 | 18:30 | 93 | Kushtia | 158 | 18:00 | 159 | Satmasjid | 103 | 13:00
28 | Bhulta | 216 | 00:00 | 94 | Laksam | 36 | 23:00 | 160 | Savar | 225 | 18:30
29 | Bog-Sherpur | 66 | 18:00 | 95 | Lakshmipur | 34 | 19:00 | 161 | SevenRings | 16.2 | 23:00
30 | Bogura | 166 | 21:00 | 96 | Lalbag | 62 | 11:00 | 162 | ShahCement | 32 | 00:00
31 | Borhanuddin | 94.7 | 19:00 | 97 | Lalmonirhat | 56 | 18:30 | 163 | Shahjadpur | 94 | 18:30
32 | Brahmanbaria | 141 | 18:30 | 98 | MI_Cement | 16.6 | 15:00 | 164 | Shahjibazar | 130 | 18:30
33 | Cantonment | 148 | 13:00 | 99 | Madanganj | 44 | 18:30 | 165 | Shahmirpur | 57 | 18:00
34 | Chandina | 20.04 | 23:00 | 100 | Madaripur | 109 | 22:00 | 166 | Shariatpur | 88 | 20:00
35 | Chandpur | 86 | 20:00 | 101 | Madartek | 100 | 23:00 | 167 | Sherpur | 124 | 07:00
36 | Chandraghona | 38 | 18:00 | 102 | Madunaghat | 62 | 18:30 | 168 | Shikalbaha | 26 | 00:00
37 | Chapai | 67 | 22:00 | 103 | Magura | 65 | 18:30 | 169 | Shitalakhya | 94.2 | 16:00
38 | Charsaidpur | 26 | 15:00 | 104 | Mahasthangarh | 72 | 00:00 | 170 | Sholosohor | 51 | 18:00
39 | Chauddagram | 78 | 19:30 | 105 | Maijdee | 36 | 19:30 | 171 | Shyampur | 152 | 12:00
40 | Chhatak | 38 | 20:00 | 106 | Manikganj | 119 | 21:00 | 172 | Siddhirganj | 123 | 12:00
41 | Chowmuhani | 183 | 19:30 | 107 | Maniknagar | 66 | 13:00 | 173 | Sirajganj | 120 | 19:00
42 | Chuadanga | 108 | 18:30 | 108 | Matarbari | 54 | 23:00 | 174 | Sonargaon | 112 | 18:30
43 | Coxsbazar | 146 | 12:00 | 109 | Matuail | 70 | 12:00 | 175 | Sreemongol | 85 | 18:30
44 | Cumilla(N) | 147 | 20:00 | 110 | Metrorail_Motijheel | 32 | 17:00 | 176 | Sreepur | 107 | 18:00
45 | Cumilla(S) | 174 | 18:00 | 111 | Metrorail_Uttara | 8 | 15:00 | 177 | Srinagar | 47.1 | 20:00
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 133 | 15:00 | 178 | Sunamganj | 63 | 19:30
47 | Daudkandi | 159 | 22:00 | 113 | Mirpur | 132 | 18:00 | 179 | Sylhet | 56 | 19:00
48 | DhakaUniversity | 96 | 13:00 | 114 | Mirsorai | 12 | 15:00 | 180 | Sylhet-132 | 145 | 18:30
49 | Dhamrai | 128 | 18:30 | 115 | Mirzapur | 39 | 03:00 | 181 | TK | 24 | 18:00
50 | Dhanmondi | 127 | 13:00 | 116 | Mithapukur | 56 | 18:30 | 182 | Tangail | 164 | 13:00
51 | Dohazari | 112 | 19:30 | 117 | Modern | N/A | N/A | 183 | Taraganj | 22 | 18:00
52 | Faridpur | 164 | 18:30 | 118 | Mogbazar | 93.3 | 15:00 | 184 | Thakurgaon | 94 | 19:00
53 | Fatullah | 122 | 16:00 | 119 | Mongla | 36 | 19:00 | 185 | Tongi | 131 | 18:00
54 | Fenchuganj | 44 | 18:30 | 120 | Motijheel | 53 | 13:00 | 186 | Ullahpara | 40 | 18:30
55 | Feni | 136 | 18:30 | 121 | Muktagacha | 32 | 19:30 | 187 | Ullon | 71 | 23:00
56 | GPH | 4 | 18:00 | 122 | Munshiganj | 117 | 19:00 | 188 | Uttara | 92 | 18:00
57 | Ghatail | 70 | 07:00 | 123 | Muradnagar | 44 | 18:30 | 189 | UttaraNew | 65 | 23:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 195 | 20:00 | 190 | Zigatola | 72 | 12:00
59 | Ghorashal-230 | 102 | 19:00 | 125 | Naogaon | 123 | 22:00
60 | Goalpara | 39 | 00:00 | 126 | Narail | 59 | 18:30
61 | Gollamari | 96 | 13:00 | 127 | Narinda | 70 | 13:00
62 | Gopalganj | 101.2 | 21:00 | 128 | Narshingdi | 182 | 22:00
63 | Gulshan | 136 | 12:00 | 129 | Natore | 144 | 21:00
64 | Halishahar | 76 | 16:00 | 130 | Nawabganj | 46.8 | 21:00
65 | HaripurSBU | 155 | 11:00 | 131 | Netrakona | 112 | 07:00
66 | Hasnabad | 93 | 21:00 | 132 | New | 60 | 15:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14453.56 | 198 |  | 14660.47
1:00 | 14142.7 | 189 |  | 14340.7
2:00 | 13828.98 | 164 |  | 13999.98
3:00 | 13220.37 | 77 |  | 13300.37
4:00 | 12891.61 | 56 |  | 12950.61
5:00 | 12457.23 | 42 |  | 12501.23
6:00 | 12178.23 | 32 |  | 12211.23
7:00 | 12339 | 0 |  | 12339
8:00 | 12441.63 | 50 |  | 12493.63
9:00 | 12576.41 | 25 |  | 12602.41
10:00 | 12694.59 | 36 |  | 12732.59
11:00 | 13054.85 | 36 |  | 13092.85
12:00 | 13404.96 | 381 |  | 13802.96
13:00 | 13671.42 | 393 |  | 14082.42
14:00 | 13656.32 | 379 |  | 14052.38
15:00 | 13708.12 | 331 |  | 14054.02
16:00 | 13585.42 | 306 |  | 13905.19
17:00 | 13503.46 | 143 |  | 13652.9
18:00 | 14547.33 | 299 |  | 14859.79
19:00 | 15546.26 | 129 |  | 15681.07
19:30 | 15415.96 | 100 |  | 15520.46
20:00 | 15382.72 | 85 |  | 15471.55
21:00 | 15257.66 | 79 |  | 15340.66
22:00 | 15129.76 | 77 |  | 15209.76
23:00 | 14725.96 | 110 |  | 14840.96
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7325.36 | 7128.2 | 14453.56 | DAILY GENERATION CURVE
00:30 | 7276.86 | 7021.27 | 14298.13
01:00 | 7228.36 | 6914.34 | 14142.7 | 21-10-2025
01:30 | 7123.68 | 6862.16 | 13985.84
02:00 | 7019 | 6809.98 | 13828.98
02:30 | 6897.7 | 6626.975 | 13524.675
03:00 | 6776.4 | 6443.97 | 13220.37
03:30 | 6711.9 | 6344.09 | 13055.99
04:00 | 6647.4 | 6244.21 | 12891.61
04:30 | 6516.9 | 6157.52 | 12674.42
05:00 | 6386.4 | 6070.83 | 12457.23
05:30 | 6302.905 | 6014.825 | 12317.73
06:00 | 6219.41 | 5958.82 | 12178.23
06:30 | 6284.005 | 5974.61 | 12258.615
07:00 | 6348.6 | 5990.4 | 12339
07:30 | 6368.78 | 6021.535 | 12390.315
08:00 | 6388.96 | 6052.67 | 12441.63
08:30 | 6418.39 | 6090.63 | 12509.02
09:00 | 6447.82 | 6128.59 | 12576.41
09:30 | 6521.505 | 6113.995 | 12635.5
10:00 | 6595.19 | 6099.4 | 12694.59
10:30 | 6741.295 | 6133.425 | 12874.72
11:00 | 6887.4 | 6167.45 | 13054.85
11:30 | 7025.225 | 6204.68 | 13229.905
12:00 | 7163.05 | 6241.91 | 13404.96
12:30 | 7207.015 | 6331.175 | 13538.19
13:00 | 7250.98 | 6420.44 | 13671.42
13:30 | 7240.94 | 6422.93 | 13663.87
14:00 | 7230.9 | 6425.42 | 13656.32
14:30 | 7271.875 | 6410.345 | 13682.22
15:00 | 7312.85 | 6395.27 | 13708.12
15:30 | 7323.85 | 6322.92 | 13646.77
16:00 | 7334.85 | 6250.57 | 13585.42
16:30 | 7362.785 | 6181.655 | 13544.44
17:00 | 7390.72 | 6112.74 | 13503.46
17:30 | 7606.46 | 6418.935 | 14025.395
18:00 | 7822.2 | 6725.13 | 14547.33
18:30 | 7974.5 | 7072.295 | 15046.795
19:00 | 8126.8 | 7419.46 | 15546.26
19:30 | 8040.36 | 7375.6 | 15415.96
20:00 | 8031.76 | 7350.96 | 15382.72
20:30 | 7982.71 | 7337.48 | 15320.19 |  | Executive Engineer
21:00 | 7933.66 | 7324 | 15257.66 |  | Network Operation Division
21:30 | 7886.71 | 7307 | 15193.71
22:00 | 7839.76 | 7290 | 15129.76
22:30 | 7699.86 | 7228 | 14927.86
23:00 | 7559.96 | 7166 | 14725.96

## En-Curve
QF-LDC-12
Date | 21-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3386 | 1567 | 903 | 38 | 90 | 1477 | 221 | 4695 | 0 | 442 | 1634.56 | 0 | 0 | 0 | 198 | DAILY ENERGY CURVE
00:30 | 3395 | 1566.5 | 903 | 38 | 92 | 1477.07 | 220.5 | 4695.5 | 0 | 380 | 1530.56 | 0 | 0 | 0 | 193.5 | 21-10-2025
01:00 | 3404 | 1566 | 903 | 38 | 94 | 1477.14 | 220 | 4696 | 0 | 318 | 1426.56 | 0 | 0 | 0 | 189
01:30 | 3393 | 1565 | 902.5 | 38 | 94 | 1477.56 | 219.5 | 4640.5 | 0 | 330.5 | 1325.28 | 0 | 0 | 0 | 176.5 | Energy Generated | 331.5778 |  | MKWHr
02:00 | 3382 | 1564 | 902 | 38 | 94 | 1477.98 | 219 | 4585 | 0 | 343 | 1224 | 0 | 0 | 0 | 164 | Energy not Served | 3.617 |  | MKWHr
02:30 | 3369.5 | 1560.2 | 902.5 | 38 | 88 | 1408.475 | 218.5 | 4594.5 | 0 | 307.5 | 1037.5 | 0 | 0 | 0 | 120.5 | Total Energy Requirement | 335.1948 |  | MKWHr
03:00 | 3357 | 1556.4 | 903 | 38 | 82 | 1338.97 | 218 | 4604 | 0 | 272 | 851 | 0 | 0 | 0 | 77
03:30 | 3351 | 1558.4 | 903 | 38 | 84 | 1275.09 | 218 | 4579 | 0 | 247.5 | 802 | 0 | 0 | 0 | 66.5
04:00 | 3345 | 1560.4 | 903 | 38 | 86 | 1211.21 | 218 | 4554 | 0 | 223 | 753 | 0 | 0 | 0 | 56
04:30 | 3354.5 | 1563.9 | 903 | 38 | 86 | 1197.52 | 218.5 | 4582 | 0 | 171 | 560 | 0 | 0 | 0 | 49
05:00 | 3364 | 1567.4 | 903 | 38 | 86 | 1183.83 | 219 | 4610 | 0 | 119 | 367 | 0 | 0 | 0 | 42
05:30 | 3349.5 | 1561.9 | 903 | 38 | 79 | 1174.825 | 219 | 4546.5 | 0.005 | 119 | 327 | 0 | 0 | 0 | 37
06:00 | 3335 | 1556.4 | 903 | 38 | 72 | 1165.82 | 219 | 4483 | 0.01 | 119 | 287 | 0 | 0 | 0 | 32
06:30 | 3369.5 | 1576.2 | 903 | 38 | 71 | 1120.985 | 219.5 | 4493 | 44.93 | 135.5 | 287 | 0 | 0 | 0 | 16
07:00 | 3404 | 1596 | 903 | 38 | 70 | 1076.15 | 220 | 4503 | 89.85 | 152 | 287 | 0 | 0 | 0 | 0
07:30 | 3403 | 1580.5 | 906.5 | 38 | 71 | 1054.075 | 220 | 4447.5 | 217.24 | 160 | 292.5 | 0 | 0 | 0 | 25
08:00 | 3402 | 1565 | 910 | 38 | 72 | 1032 | 220 | 4392 | 344.63 | 168 | 298 | 0 | 0 | 0 | 50
08:30 | 3406 | 1566 | 913 | 38 | 72.5 | 1031.5 | 220.5 | 4352.5 | 442.02 | 168.5 | 298.5 | 0 | 0 | 0 | 37.5
09:00 | 3410 | 1567 | 916 | 38 | 73 | 1031 | 221 | 4313 | 539.41 | 169 | 299 | 0 | 0 | 0 | 25
09:30 | 3406 | 1582.5 | 916 | 38 | 71.5 | 1003.5 | 221 | 4263.5 | 606 | 177 | 350.5 | 0 | 0 | 0 | 30.5
10:00 | 3402 | 1598 | 916 | 38 | 70 | 976 | 221 | 4214 | 672.59 | 185 | 402 | 0 | 0 | 0 | 36
10:30 | 3422 | 1575 | 919 | 38 | 74.5 | 980 | 221 | 4170.5 | 695.72 | 180.5 | 598.5 | 0 | 0 | 0 | 36
11:00 | 3442 | 1552 | 922 | 38 | 79 | 984 | 221 | 4127 | 718.85 | 176 | 795 | 0 | 0 | 0 | 36
11:30 | 3443.5 | 1552.5 | 926 | 38 | 79.5 | 1002.5 | 221 | 4174 | 724.405 | 187.5 | 881 | 0 | 0 | 0 | 208.5
12:00 | 3445 | 1553 | 930 | 38 | 80 | 1021 | 221 | 4221 | 729.96 | 199 | 967 | 0 | 0 | 0 | 381
12:30 | 3433.5 | 1553 | 930 | 38 | 82 | 1067 | 220.5 | 4278.5 | 706.69 | 209 | 1020 | 0 | 0 | 0 | 387
13:00 | 3422 | 1553 | 930 | 38 | 84 | 1113 | 220 | 4336 | 683.42 | 219 | 1073 | 0 | 0 | 0 | 393
13:30 | 3421.5 | 1545.5 | 929.5 | 38 | 84 | 1142.5 | 220 | 4355.5 | 638.37 | 214 | 1075 | 0 | 0 | 0 | 386
14:00 | 3421 | 1538 | 929 | 38 | 84 | 1172 | 220 | 4375 | 593.32 | 209 | 1077 | 0 | 0 | 0 | 379
14:30 | 3424.5 | 1554 | 929.5 | 38 | 88 | 1185.605 | 220 | 4405 | 521.365 | 209.5 | 1106.75 | 0 | 0 | 0 | 355
15:00 | 3428 | 1570 | 930 | 38 | 92 | 1199.21 | 220 | 4435 | 449.41 | 210 | 1136.5 | 0 | 0 | 0 | 331
15:30 | 3422 | 1577.5 | 930 | 38 | 93 | 1207.1 | 218 | 4412.5 | 338.92 | 221 | 1188.25 | 0 | 0 | 0.5 | 318.5
16:00 | 3416 | 1585 | 930 | 38 | 94 | 1214.99 | 216 | 4390 | 228.43 | 232 | 1240 | 0 | 0 | 1 | 306
16:30 | 3354.5 | 1574.5 | 929.5 | 38 | 88 | 1295.715 | 216 | 4353.5 | 130.825 | 244.5 | 1318.4 | 0 | 0 | 1 | 224.5
17:00 | 3293 | 1564 | 929 | 38 | 82 | 1376.44 | 216 | 4317 | 33.22 | 257 | 1396.8 | 0 | 0 | 1 | 143
17:30 | 3272 | 1583 | 929 | 38 | 91 | 1426.285 | 217 | 4397.5 | 16.61 | 466.5 | 1588 | 0 | 0 | 0.5 | 221
18:00 | 3251 | 1602 | 929 | 38 | 100 | 1476.13 | 218 | 4478 | 0 | 676 | 1779.2 | 0 | 0 | 0 | 299
18:30 | 3329.5 | 1648.5 | 929.5 | 38 | 93 | 1473.295 | 218 | 4678 | 0 | 757 | 1882 | 0 | 0 | 0 | 214
19:00 | 3408 | 1695 | 930 | 38 | 86 | 1470.46 | 218 | 4878 | 0 | 838 | 1984.8 | 0 | 0 | 0 | 129
19:30 | 3418 | 1688 | 929 | 38 | 90 | 1478.6 | 218 | 4804 | 0 | 850 | 1902.36 | 0 | 0 | 0 | 100
20:00 | 3398 | 1692 | 929 | 38 | 88 | 1472.96 | 220 | 4810 | 0 | 838 | 1896.76 | 0 | 0 | 0 | 85
20:30 | 3391 | 1657.5 | 929.5 | 38 | 90 | 1468.98 | 220 | 4806.5 | 0 | 839.5 | 1879.21 | 0 | 0 | 0 | 82
21:00 | 3384 | 1623 | 930 | 38 | 92 | 1465 | 220 | 4803 | 0 | 841 | 1861.66 | 0 | 0 | 0 | 79
21:30 | 3374.5 | 1613 | 930 | 38 | 95 | 1462.5 | 220 | 4792 | 0 | 835 | 1833.71 | 0 | 0 | 0 | 78
22:00 | 3365 | 1603 | 930 | 38 | 98 | 1460 | 220 | 4781 | 0 | 829 | 1805.76 | 0 | 0 | 0 | 77
22:30 | 3323.5 | 1587 | 930 | 38 | 98 | 1464.5 | 220.5 | 4770 | 0 | 698 | 1798.36 | 0 | 0 | 0 | 93.5
23:00 | 3282 | 1571 | 930 | 38 | 98 | 1469 | 221 | 4759 | 0 | 567 | 1790.96 | 0 | 0 | 0 | 110
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 21-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 376 | 06:00 | 237 | 00:00 | Payra | 410 | 08:00 | 404 | 18:00
Ashuganj | 403 | 6:00 | 396 | 00:00 | Rahanpur | 399 | 04:00 | 383 | 18:30
Bhulta | 396 | 06:00 | 373 | 11:00 | Rampal | 403 | 06:00 | 390 | 18:30
Bibiana | 385 | 18:00 | 378 | 00:00
BIPTC | 403 | 06:00 | 395 | 00:00
Bogura | 390 | 04:00 | 368 | 18:30
Gopalganj | 392 | 06:00 | 379 | 18:30
Kaliakoir | 367 | 04:00 | 356 | 14:00
Madunaghat | 391 | 18:00 | 386 | 10:00
Meghnaghat | 378 | 06:00 | 370 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 17:00 | 215 | 11:00 | Kaliakoir | 228 | 04:00 | 220 | 14:00
AKSML | 230 | 18:00 | 223 | 09:00 | Keranigonj | 221 | 06:00 | 212 | 10:00
Aminbazar | 223 | 05:00 | 27 | 10:00 | Khulna(S) | 233 | 06:00 | 218 | 18:30
Ashuganj | 230 | 21:00 | 216 | 10:00 | Madunaghat | 230 | 00:00 | 226 | 07:00
Ashuganj-400 | 230 | 21:00 | 216 | 10:00 | Madunaghat-400 | 231 | 00:00 | 227 | 09:00
Baghabari | 235 | 06:00 | 224 | 14:00 | Maniknagar | 214 | 06:00 | 209 | 10:00
Barapukuria | 220 | 01:00 | 202 | 18:30 | Meghnaghat | 222 | 00:00 | 217 | 11:00
Barapukuria-230 | 220 | 01:00 | 202 | 18:30 | Meghnaghat-400 | 219 | 04:00 | 213 | 09:00
Barishal | 233 | 08:00 | 226 | 19:00 | Mirsorai | 231 | 18:00 | 217 | 07:00
Bheramara | 235 | 04:00 | 223 | 18:30 | Rajshahi | 234 | 04:00 | 222 | 13:00
Bhulta | 225 | 04:00 | 210 | 10:00 | Rampal | 231 | 06:00 | 219 | 18:30
Bibiana | 226 | 18:00 | 221 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 238 | 04:00 | 222 | 18:30 | Rampura | 223 | 04:00 | 207 | 13:00
Bogura | 237 | 04:00 | 224 | 18:30 | Shikalbaha | 230 | 00:00 | 223 | 09:00
Bogura-400 | 238 | 04:00 | 223 | 18:30 | Shyampur | 220 | 06:00 | 211 | 11:00
Borhanuddin | 236 | 05:00 | 230 | 23:00 | Siddhirganj | 215 | 22:00 | 212 | 03:00
BSRM | 228 | 18:00 | 216 | 07:00 | Sirajgonj | 237 | 03:00 | 230 | 18:30
Cumilla(N) | 222 | 18:00 | 213 | 09:00 | Sreepur | 224 | 18:00 | 215 | 11:00
Faridpur | 230 | 06:00 | 221 | 18:30 | Tongi | 220 | 04:00 | 212 | 00:00
Fenchuganj | 228 | 06:00 | 223 | 00:00
Ghorashal | 230 | 05:00 | 220 | 00:00
Ghorashal-230 | 222 | 04:00 | 210 | 11:00
Gopalganj | 231 | 06:00 | 224 | 18:30
GPH | 230 | 18:00 | 222 | 09:00
Haripur | 216 | 06:00 | 211 | 10:00
Hasnabad | 220 | 04:00 | 212 | 11:00
Hathazari | 228 | 02:00 | 221 | 09:00
Ishurdi | 237 | 04:00 | 224 | 18:30
Jhenaidah | 234 | 06:00 | 215 | 18:30
Kachua | 228 | 17:00 | 121 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 128 | 11:00 | Lalmonirhat | 130 | 23:00 | 120 | 07:00
Agargaon | 131 | 04:00 | 124 | 11:00 | Madanganj | 128 | 12:00 | 124 | 05:00
Agrabad | 130 | 00:00 | 126 | 09:00 | Madaripur | 134 | 05:00 | 129 | 18:30
AKS | 129 | 00:00 | 8 | 14:00 | Madartek | 136 | 05:00 | 123 | 03:00
Aminbazar | 131 | 05:00 | 125 | 11:00 | Madunaghat | 133 | 00:00 | 130 | 07:00
Amnura | 136 | 00:00 | 128 | 13:00 | Magura | 136 | 06:00 | 121 | 18:30
Ashuganj | 137 | 18:00 | 132 | 00:00 | Mahasthangarh | 132 | 04:00 | 122 | 18:30
Bagerhat | 132 | 09:00 | 113 | 18:30 | Maijdee | 132 | 16:00 | 30 | 14:00
Bajitpur | 129 | 18:00 | 120 | 11:00 | Manikganj | 126 | 05:00 | 118 | 10:00
Bakulia | 132 | 00:00 | 128 | 09:00 | Maniknagar | 129 | 05:00 | 124 | 11:00
Banani | 137 | 04:00 | 126 | 12:00 | Matarbari | 119 | 10:00 | 107 | 18:30
Bangabhaban | 130 | 06:00 | 124 | 10:00 | Matuail | 125 | 05:00 | 122 | 10:00
Barapukuria | 135 | 01:00 | 122 | 18:30 | Metrorail_Motijheel | 129 | 05:00 | 124 | 11:00
Barguna | 135 | 09:00 | 132 | 00:00 | Metrorail_Uttara | 128 | 06:00 | 119 | 13:00
Barishal | 135 | 05:00 | 128 | 14:00 | Millgate | 130 | 03:00 | 121 | 11:00
Barishal-230 | 134 | 06:00 | 128 | 15:00 | Mirpur | 131 | 05:00 | 124 | 10:00
Baroaulia | 132 | 13:00 | 128 | 06:00 | Mirzapur | 130 | 06:00 | 122 | 19:30
Baroirhat | 131 | 16:00 | 125 | 07:00 | Mithapukur | 138 | 20:00 | 120 | 18:30
Bashundhara | 137 | 04:00 | 125 | 14:00 | MI_Cement | 129 | 05:00 | 120 | 11:00
BashundharaCement | 128 | 12:00 | 124 | 05:00 | Modern | 0 | 00:00 | 0 | 00:00
Beanibazar | 128 | 06:00 | 122 | 19:00 | Mogbazar | 136 | 05:00 | 127 | 11:00
Benapole | 134 | 05:00 | 116 | 18:30 | Mongla | 131 | 08:00 | 115 | 18:30
Bhaluka | 129 | 18:00 | 118 | 15:00 | Motijheel | 130 | 05:00 | 124 | 10:00
Bhandaria | 128 | 09:00 | 107 | 18:30 | Muktagacha | 130 | 08:00 | 116 | 21:00
Bhangura | 134 | 04:00 | 127 | 18:30 | Munshiganj | 125 | 22:00 | 120 | 10:00
Bheramara | 138 | 04:00 | 132 | 18:30 | Muradnagar | 126 | 17:00 | 120 | 10:00
Bheramara(GK) | 138 | 05:00 | 132 | 18:30 | Mymensingh | 130 | 08:00 | 112 | 14:00
Bhulta | 122 | 04:00 | 120 | 00:00 | Naogaon | 129 | 06:00 | 121 | 18:30
Bog-Sherpur | 134 | 04:00 | 125 | 18:30 | Narail | 137 | 06:00 | 120 | 18:30
Bogura | 135 | 04:00 | 127 | 13:00 | Narinda | 129 | 05:00 | 124 | 11:00
Bogura-230 | 135 | 04:00 | 127 | 18:30 | Narshingdi | 127 | 06:00 | 116 | 10:00
Brahmanbaria | 130 | 06:00 | 124 | 00:00 | Natore | 134 | 04:00 | 127 | 18:30
Cantonment | 131 | 04:00 | 123 | 13:00 | Nawabganj | 131 | 06:00 | 124 | 10:00
Chandina | 130 | 18:00 | 124 | 10:00 | Netrakona | 123 | 18:00 | 112 | 14:00
Chandpur | 138 | 17:00 | 128 | 07:00 | New | 130 | 06:00 | 121 | 14:00
Chandraghona | 134 | 00:00 | 131 | 09:00 | Niamatpur | 136 | 05:00 | 129 | 18:30
Chapai | 135 | 14:00 | 128 | 18:30 | Noapara | 134 | 08:00 | 122 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 125 | 22:00 | 121 | 11:00 | Pabna | 136 | 04:00 | 128 | 18:30
Chauddagram | 130 | 16:00 | 123 | 10:00 | Palashbari | 127 | 16:00 | 117 | 18:30
Chhatak | 127 | 06:00 | 119 | 18:30 | Panchagarh | 140 | 02:00 | 34 | 01:00
Chowmuhani | 132 | 17:00 | 123 | 07:00 | Patiya | 130 | 00:00 | 127 | 05:00
Chuadanga | 136 | 06:00 | 120 | 18:30 | Patuakhali | 135 | 01:00 | 133 | 00:00
Coxsbazar | 118 | 04:00 | 108 | 18:00 | Payra | 136 | 05:00 | 134 | 18:30
Cumilla(N) | 129 | 16:00 | 124 | 09:00 | PHP | 131 | 17:00 | 124 | 07:00
Cumilla(S) | 130 | 04:00 | 119 | 13:00 | Postogola | 130 | 04:00 | 123 | 10:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 137 | 04:00 | 126 | 13:00
Daudkandi | 123 | 05:00 | 117 | 19:00 | Purbasadipur | 135 | 02:00 | 118 | 14:00
DhakaUniversity | 137 | 04:00 | 127 | 11:00 | Rahanpur | 137 | 06:00 | 131 | 18:30
Dhamrai | 130 | 06:00 | 123 | 14:00 | Rahanpur-400 | 137 | 04:00 | 131 | 18:30
Dhanmondi | 138 | 06:00 | 127 | 11:00 | Rahim | 126 | 05:00 | 122 | 10:00
Dohazari | 127 | 23:00 | 122 | 05:00 | Rajbari | 135 | 08:00 | 128 | 18:30
Faridpur | 135 | 06:00 | 130 | 00:00 | Rajendrapur | 129 | 17:00 | 117 | 14:00
Fatullah | 133 | 06:00 | 126 | 13:00 | Rajshahi | 134 | 04:00 | 126 | 13:00
Fenchuganj | 134 | 06:00 | 130 | 18:30 | Rajshahi-230 | 134 | 03:00 | 127 | 13:00
Feni | 130 | 16:00 | 123 | 10:00 | Ramganj | 133 | 18:00 | 124 | 07:00
Ghatail | 128 | 05:00 | 116 | 19:30 | Rampur | 130 | 00:00 | 126 | 09:00
Ghorashal | 134 | 18:00 | 126 | 10:00 | Rampura | 137 | 04:00 | 126 | 13:00
Goalpara | 135 | 06:00 | 123 | 18:30 | Rangamati | 133 | 05:00 | 130 | 10:00
Gollamari | 135 | 06:00 | 125 | 18:30 | Rangpur | 134 | 03:00 | 122 | 14:00
Gopalganj | 134 | 06:00 | 126 | 18:30 | Ruppur | 139 | 06:00 | 132 | 18:30
Gopalganj-400 | 135 | 06:00 | 130 | 18:30 | Saidpur | 132 | 04:00 | 117 | 18:30
Gulshan | 137 | 05:00 | 127 | 11:00 | Satkhira | 132 | 09:00 | 118 | 18:30
Halishahar | 131 | 00:00 | 127 | 09:00 | Satmasjid | 130 | 04:00 | 123 | 13:00
Haripur | 126 | 06:00 | 123 | 10:00 | Savar | 131 | 18:00 | 122 | 10:00
HaripurSBU | 126 | 06:00 | 123 | 10:00 | SevenRings | 134 | 06:00 | 126 | 10:00
Hasnabad | 131 | 05:00 | 123 | 11:00 | ShahCement | 125 | 22:00 | 121 | 11:00
Hathazari | 134 | 17:00 | 130 | 08:00 | Shahjadpur | 136 | 02:00 | 131 | 13:00
Ishurdi | 139 | 04:00 | 132 | 18:30 | Shahjibazar | 131 | 06:00 | 125 | 00:00
Jaldhaka | 129 | 01:00 | 114 | 18:30 | Shahmirpur | 131 | 00:00 | 128 | 09:00
Jamalpur | 131 | 08:00 | 116 | 19:30 | Shariatpur | 134 | 08:00 | 127 | 18:30
Jashore | 134 | 05:00 | 118 | 18:30 | Sherpur | 130 | 08:00 | 112 | 20:00
Jhenaidah | 138 | 06:00 | 122 | 18:30 | Shikalbaha | 124 | 01:00 | 119 | 13:00
Jhenaidah-230 | 139 | 06:00 | 125 | 18:30 | Shikalbaha-230 | 133 | 00:00 | 129 | 09:00
Joydebpur | 132 | 06:00 | 101 | 11:00 | Shitalakhya | 129 | 05:00 | 120 | 11:00
Joypurhat | 128 | 06:00 | 118 | 18:30 | Sholosohor | 133 | 00:00 | 130 | 09:00
Juldah | 132 | 00:00 | 127 | 09:00 | Shyampur | 130 | 01:00 | 127 | 09:00
Kabirpur | 132 | 18:00 | 118 | 11:00 | Shyampur-230 | 132 | 04:00 | 127 | 10:00
Kachua | 136 | 17:00 | 126 | 07:00 | Siddhirganj | 125 | 03:00 | 122 | 10:00
Kaliakoir | 133 | 04:00 | 125 | 14:00 | Sirajganj | 132 | 02:00 | 123 | 18:30
Kallyanpur | 133 | 06:00 | 125 | 10:00 | Sonargaon | 125 | 18:00 | 121 | 09:00
Kalurghat | 134 | 00:00 | 131 | 07:00 | Sreemongol | 130 | 06:00 | 125 | 00:00
Kamrangirchar | 131 | 06:00 | 122 | 16:00 | Sreepur | 131 | 18:00 | 123 | 11:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 130 | 04:00 | 124 | 00:00
Kasba | 126 | 17:00 | 120 | 19:00 | SSM | 136 | 17:00 | 132 | 00:00
Kazla | 131 | 03:00 | 124 | 11:00 | Sunamganj | 126 | 09:00 | 117 | 18:30
Keranigonj | 131 | 05:00 | 124 | 10:00 | Sylhet | 129 | 07:00 | 124 | 18:30
Khagrachori | 132 | 00:00 | 129 | 09:00 | Sylhet-132 | 130 | 07:00 | 125 | 18:30
Khulna | 134 | 06:00 | 122 | 18:30 | Tangail | 128 | 04:00 | 117 | 19:30
Khulna(S) | 135 | 06:00 | 124 | 18:30 | Taraganj | 132 | 23:00 | 116 | 18:30
Khulshi | 130 | 00:00 | 126 | 10:00 | Thakurgaon | 136 | 02:00 | 116 | 07:00
Kishoreganj | 128 | 18:00 | 117 | 14:00 | TK | 133 | 00:00 | 130 | 09:00
Kodda | 132 | 18:00 | 119 | 11:00 | Tongi | 131 | 04:00 | 124 | 10:00
KSRM | 133 | 16:00 | 128 | 07:00 | Ullahpara | 134 | 05:00 | 125 | 18:30
Kulaura | 134 | 07:00 | 129 | 18:30 | Ullon | 137 | 04:00 | 126 | 13:00
Kurigram | 130 | 04:00 | 114 | 18:30 | Uttara | 131 | 05:00 | 123 | 10:00
Kushtia | 136 | 06:00 | 127 | 18:30 | UttaraNew | 128 | 06:00 | 119 | 13:00
Laksam | 134 | 17:00 | 125 | 07:00 | Zigatola | 131 | 06:00 | 124 | 11:00
Lakshmipur | 131 | 16:00 | 122 | 10:00
Lalbag | 131 | 06:00 | 123 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division