## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-10-2025 | during | 24-10-2025 | during | 24-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 404 | 413 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 93 | 97 | 208.13 | 208.13 | 94 | 94 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 328 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 140 | 149.36 | 149.36 | 45 | 120 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19.5 | 21.5 | 24.75 | 24.75 | 24.75 | 24.75 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 24 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 65 | 130 | 300 | 300 | 64 | 95 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 51 | 62 | 0 | 0 | 35 | 70 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 144 | 162 | 162 | 108 | 108 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 0 | 0 | 70 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1761.5 | 2292.5 | 4937.15 | 4904.15 | 3577.5 | 3868.5
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 16 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 12 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 151 | 149 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 39 | 69 | 40 | 70 | 40 | 70 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 63 | 75 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 20 | 35 | 35 | 35 | 35 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 24 | 99 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.35 | 0 | 3.55 | 0 | 3.55 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 35 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 68 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 86 | 85 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 160 | 159.86 | 159.86 | 17 | 159 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1158 | 1134 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2521.35 | 2878 | 3468.27 | 3483.72 | 2747.91 | 2939.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 339 | 351 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 340 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 34 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 39 | 42 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 63 | 63 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 76 | 112 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 40 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 101 | 163 | 163 | 105 | 105 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 170 | 170 | 200 | 200 | 180 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 78 | 90 | 160 | 160 | 98 | 98 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 20.83 | 20.83 | Schedule Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 95 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 70 | 115 | 115 | 90 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 51 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1586 | 1619 | 2280.38 | 2220.38 | 1971.38 | 1920.38
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-10-2025 | during | 24-10-2025 | during | 24-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 83 | 73 | 0 | 0 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 47 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 58 | 48 | 48 | 48 | 48 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.98 | 0 | 41.12 | 0 | 41.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 249.98 | 195 | 215.92 | 172.5 | 162.42 | 119
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 66 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 146 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 160 | 161 | 0 | 0 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 0 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 0 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 312 | 312 | 325 | 325 | 325 | 325 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1129 | 1120 | 1038 | 1038 | 1216 | 1216
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 931 | 930 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 63 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 378 | 360 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 86 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 978 | 1148 | 0 | 0 | 1096 | 1096 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2411 | 2580 | 2408 | 2318 | 2743 | 2653
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 302 | 408 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 16 | 32 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1085 | 1202 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 9 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 170 | 180 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.51 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1887.51 | 2161 | 2147 | 2146 | 1920 | 1935
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 59.73 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 175 | 166 | 214 | 214 | 214 | 214 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 405 | 333 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 18 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 111 | 113 | 113 | 35 | 113 | Fuel shortage as BPDB payment not done in time
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.3 | 0 | 5.55 | 0 | 5.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1043.09 | 1462 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 59.87 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 109 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1856.99 | 2354.2 | 3180.42 | 3013.87 | 2992.42 | 2903.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 110 | 0 | 180.91 | 0 | 180.91 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 187.6 | 222 | 464.91 | 248 | 444.91 | 228
System Total |  |  |  |  | 28823.2 | 28364.092 | 13590.93 | 15421.7 | 20140.05 | 19544.62 | 17775.54 | 17783.11
Forecast Scenario (24-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14550 |  | 0 |  | 14550
|  |  |  | 1:00 | 14110 |  | 0 |  | 14110
|  |  |  | 2:00 | 13720 |  | 0 |  | 13720
|  |  |  | 3:00 | 13050 |  | 0 |  | 13050
|  |  |  | 4:00 | 12790 |  | 0 |  | 12790
|  |  |  | 5:00 | 12390 |  | 0 |  | 12390
|  |  |  | 6:00 | 12170 |  | 0 |  | 12170
|  |  |  | 7:00 | 11950 |  | 0 |  | 11950
|  |  |  | 8:00 | 11880 |  | 0 |  | 11880
|  |  |  | 9:00 | 11620 |  | 0 |  | 11620
|  |  |  | 10:00 | 11660 |  | 0 |  | 11660
|  |  |  | 11:00 | 12120 |  | 0 |  | 12120
|  |  |  | 12:00 | 12870 |  | 0 |  | 12870
|  |  |  | 13:00 | 13290 |  | 0 |  | 13290
|  |  |  | 14:00 | 12740 |  | 0 |  | 12740
|  |  |  | 15:00 | 12820 |  | 0 |  | 12820
|  |  |  | 16:00 | 12380 |  | 0 |  | 12380
|  |  |  | 17:00 | 12060 |  | 0 |  | 12060
|  |  |  | 18:00 | 13720 |  | 0 |  | 13720
|  |  |  | 18:30 | 14050 |  | 0 |  | 14050
|  |  |  | 19:00 | 14510 |  | 0 |  | 14510
|  |  |  | 19:30 | 14460 |  | 0 |  | 14460
|  |  |  | 20:00 | 14450 |  | 0 |  | 14450
|  |  |  | 21:00 | 13990 |  | 0 |  | 13990
|  |  |  | 22:00 | 14600 |  | 0 |  | 14600
|  |  |  | 23:00 | 14570 |  | 0 |  | 14570
Probable Maximum Temperature: |  |  | 33.20°C
Probable Maximum Demand at Day Peak: |  |  | 12870.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14510.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14510.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 314.01 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:06 hrs on 24-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-10-2025 | [28 empty] | Date: | 23-10-2025 | [28 empty] | Date: | 23-10-2025 | [28 empty] | Date: | 23-10-2025 | [28 empty] | Date: | 23-10-2025 | [14 empty] | Date: | 23-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [14 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 17 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 17 | 17 | 27 | 45 | 67 | 15 | 0 | 72 | 0 | 450 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 17 | 21.5 | 22 | 0 | 0 | 90 | 16 | 25 | 0 | 0 | 66 | 58 | 17 | 67 | 75 | 0 | 222 | 0 | 26 | 650 | 17 | 0 | 0 | 17 | 0 | 148 | 0 | 0 | 0 | 1175 | 0 | 51 | 130 | 45 | 395 | 349 | 0 | 42 | 0 | 34 | 58 | 102 | 198 | 0 | 20 | 15 | 92 | 25 | 0 | 41 | 310 | 0 | 312 | 0 | 67 | 154 | 10 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 87 | 0 | 0 | 0 | 7219.5 | 929 | 336 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1186 | 0 | 1468.28 | 0 | 0 | 0 | 0 | 113 | 0 | 87 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 565 | 1108 | 0 | 7168.28 | 14387.78 | 105.4
01:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 17 | 17 | 30 | 75 | 15 | 0 | 35 | 0 | 450 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 17 | 21.5 | 22 | 0 | 0 | 82 | 16 | 24 | 0 | 0 | 66 | 58 | 17 | 67 | 75 | 0 | 221 | 0 | 35 | 650 | 17 | 0 | 0 | 8 | 0 | 148 | 0 | 0 | 0 | 1150 | 0 | 51 | 130 | 68 | 395 | 354 | 0 | 42 | 0 | 37 | 64 | 102 | 192 | 0 | 20 | 94 | 82 | 43 | 0 | 41 | 305 | 0 | 312 | 0 | 67 | 150 | 10 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 87 | 0 | 0 | 0 | 7163.5 | 930 | 337 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1184 | 0 | 1457.74 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 499 | 1085 | 0 | 6899.74 | 14063.24 | 105.37
02:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 17 | 17 | 30 | 63 | 15 | 0 | 35 | 0 | 450 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 17 | 21.5 | 22 | 0 | 0 | 86 | 16 | 25 | 0 | 0 | 50 | 51 | 17 | 67 | 75 | 0 | 219 | 0 | 35 | 650 | 17 | 0 | 0 | 8 | 0 | 148 | 0 | 0 | 0 | 1180 | 0 | 51 | 132 | 78 | 395 | 349 | 0 | 42 | 0 | 37 | 69 | 102 | 170 | 0 | 20 | 99 | 80 | 43 | 0 | 41 | 310 | 0 | 312 | 0 | 67 | 154 | 10 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 87 | 0 | 0 | 1 | 7162.5 | 930 | 337 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1155 | 0 | 1462.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 401 | 1090 | 0 | 6456.35 | 13618.85 | 105.36
03:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 17 | 17 | 30 | 63 | 15 | 0 | 35 | 0 | 450 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 51 | 0 | 68 | 75 | 0 | 219 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1185 | 0 | 51 | 132 | 45 | 395 | 351 | 0 | 42 | 0 | 37 | 69 | 103 | 172 | 0 | 17 | 0 | 76 | 0 | 0 | 13 | 310 | 0 | 312 | 0 | 67 | 154 | 8 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 102 | 0 | 0 | 6 | 6795.5 | 931 | 341 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1094 | 0 | 1464.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 402 | 1100 | 0 | 6420.07 | 13215.57 | 105.35
04:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 17 | 17 | 30 | 63 | 15 | 0 | 35 | 0 | 450 | 0 | 0 | 0 | 30 | 330 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 62 | 0 | 219 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1185 | 0 | 51 | 80 | 45 | 395 | 352 | 0 | 42 | 0 | 37 | 53 | 104 | 120 | 0 | 17 | 0 | 74 | 0 | 0 | 0 | 310 | 0 | 312 | 0 | 67 | 154 | 8 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 102 | 0 | 0 | 6 | 6601.5 | 930 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 1328.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 393 | 1102 | 0 | 6284.4 | 12885.9 | 105.34
05:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 17 | 17 | 30 | 0 | 0 | 0 | 35 | 0 | 450 | 0 | 0 | 0 | 17 | 331 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 62 | 0 | 219 | 0 | 39 | 650 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1185 | 0 | 51 | 12 | 45 | 395 | 353 | 0 | 43 | 0 | 37 | 51 | 104 | 68 | 0 | 17 | 0 | 74 | 0 | 0 | 0 | 310 | 0 | 312 | 0 | 67 | 153 | 8 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 102 | 0 | 0 | 6 | 6394.5 | 930 | 351 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 1318.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 303 | 1096 | 0 | 6146.12 | 12540.62 | 105.33
06:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 17 | 17 | 30 | 0 | 0 | 0 | 35 | 0 | 450 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 17 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 62 | 0 | 219 | 0 | 40 | 650 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 1170 | 0 | 51 | 0 | 45 | 395 | 352 | 0 | 43 | 0 | 37 | 37 | 104 | 65 | 0 | 17 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 312 | 0 | 67 | 157 | 8 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 102 | 0 | 0 | 6 | 6351.5 | 930 | 359 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 0 | 1230.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 301 | 1050 | 0 | 5952.95 | 12304.45 | 105.32
07:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 17 | 17 | 17 | 30 | 0 | 0 | 0 | 35 | 0 | 450 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 5 | 17 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 75 | 62 | 0.51 | 220 | 0 | 27 | 650 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 1132 | 5 | 51 | 0 | 63 | 395 | 352 | 0 | 43 | 0 | 37 | 34 | 102 | 78 | 0 | 17 | 0 | 72 | 0 | 13 | 0 | 320 | 0 | 312 | 0 | 67 | 158 | 8 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 94 | 0 | 5.59 | 6 | 6361.6 | 930 | 363 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 1052 | 0 | 1228.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.94 | 15 | 0 | 0 | 8.86 | 180 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0.72 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0.2 | 35 | 0.07 | 0 | 170 | 110 | 220 | 0 | 304 | 1074 | 0 | 6153.57 | 12515.17 | 105.31
08:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 17 | 17 | 17 | 30 | 0 | 0 | 0 | 35 | 0 | 450 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 14 | 70 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 36 | 1.47 | 220 | 0 | 7 | 650 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 1150 | 10 | 51 | 0 | 63 | 385 | 320 | 0 | 43 | 0 | 37 | 16 | 102 | 109 | 0 | 17 | 0 | 72 | 0 | 34 | 0 | 305 | 0 | 312 | 0 | 67 | 154 | 8 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 85 | 1 | 18.24 | 6 | 6291.21 | 930 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36.91 | 1038 | 0 | 1182.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.8 | 46 | 0 | 0 | 26.69 | 166 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 2.31 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 2.7 | 82 | 0.14 | 0 | 170 | 110 | 220 | 0 | 303 | 1095 | 0 | 6156.73 | 12447.94 | 105.3
09:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 17 | 17 | 45 | 0 | 0 | 17 | 35 | 0 | 450 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 22 | 70 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 48 | 36 | 1.98 | 220 | 0 | 2 | 650 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 1173 | 15 | 51 | 0 | 63 | 350 | 320 | 0 | 43 | 0 | 36 | 15 | 102 | 68 | 0 | 17 | 0 | 64 | 0 | 53 | 0 | 310 | 0 | 312 | 0 | 67 | 152 | 8 | 0 | 80 | 30 | 0 | 0 | 160 | 17 | 48 | 48 | 85 | 2 | 30.38 | 6 | 6294.36 | 931 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 60 | 1035 | 0 | 1182.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.32 | 72 | 0 | 0 | 41.51 | 159 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 3.56 | 0 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 3.8 | 131 | 0.39 | 0 | 170 | 110 | 220 | 0 | 302 | 1095 | 0 | 6270.33 | 12564.69 | 105.28
10:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 17 | 32 | 45 | 50 | 0 | 35 | 35 | 0 | 450 | 0 | 0 | 0 | 17 | 326 | 0 | 0 | 28 | 70 | 20 | 22 | 0 | 0 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 50 | 3 | 221 | 0 | 2 | 650 | 17 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 1157 | 18 | 51 | 8 | 63 | 393 | 345 | 0 | 42 | 0 | 36 | 22 | 100 | 60 | 0 | 17 | 28 | 64 | 1 | 64 | 0 | 315 | 0 | 312 | 0 | 67 | 155 | 8 | 0 | 80 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 85 | 2 | 38.93 | 6 | 6633.93 | 931 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 76 | 1030 | 0 | 1039.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.1 | 86 | 0 | 0 | 41.82 | 166 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 4.75 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 5.7 | 149 | 0.53 | 0 | 170 | 110 | 220 | 0 | 302 | 1050 | 0 | 6149.61 | 12783.54 | 105.26
11:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 45 | 45 | 81 | 0 | 35 | 35 | 0 | 450 | 0 | 0 | 0 | 35 | 325 | 0 | 0 | 31 | 52 | 20 | 22 | 0 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 23 | 0 | 63 | 62 | 3.31 | 221 | 0 | 2 | 650 | 17 | 0 | 0 | 5 | 0 | 142 | 0 | 0 | 0 | 1153 | 18 | 51 | 13 | 63 | 393 | 339 | 0 | 38 | 0 | 36 | 34 | 99 | 170 | 0 | 17 | 104 | 72 | 22 | 40 | 0 | 325 | 0 | 312 | 0 | 67 | 159 | 8 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 83 | 2 | 45.98 | 6 | 7001.29 | 931 | 365 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 84 | 1002 | 0 | 1012.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.75 | 108 | 0 | 0 | 52.62 | 172 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 5.04 | 0 | 0 | 35 | 30 | 0 | 0 | 0 | 0 | 0 | 179 | 0.58 | 0 | 170 | 110 | 220 | 0 | 303 | 1050 | 0 | 6336.21 | 13337.5 | 105.24
12:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 51 | 45 | 65 | 0 | 35 | 35 | 0 | 450 | 0 | 0 | 0 | 35 | 322 | 93 | 0 | 31 | 52 | 19.5 | 22 | 0 | 0 | 86 | 16 | 24 | 0 | 0 | 0 | 39 | 0 | 63 | 68 | 3.35 | 221 | 0 | 5 | 650 | 17 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1158 | 12 | 51 | 76 | 63 | 393 | 339 | 0 | 39 | 0 | 36 | 34 | 98 | 170 | 0 | 17 | 98 | 78 | 43 | 51 | 0 | 315 | 0 | 312 | 0 | 67 | 154 | 8 | 0 | 83 | 30 | 0 | 0 | 160 | 17 | 49 | 48 | 83 | 2 | 44.98 | 6 | 7247.83 | 931 | 378 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 86 | 978 | 0 | 1043.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.73 | 109 | 0 | 0 | 59.87 | 175 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 5.3 | 0 | 0 | 35 | 36 | 0 | 0 | 0 | 0 | 6.6 | 110 | 0.51 | 0 | 170 | 110 | 220 | 0 | 302 | 1085 | 0 | 6343.1 | 13590.93 | 105.22
13:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 17 | 51 | 44 | 65 | 4 | 35 | 35 | 0 | 450 | 0 | 0 | 0 | 35 | 320 | 94 | 0 | 29 | 70 | 19 | 22 | 0 | 0 | 85 | 16 | 66 | 0 | 0 | 0 | 39 | 0 | 63 | 82 | 3.11 | 221 | 0 | 10 | 650 | 17 | 0 | 0 | 8 | 0 | 149 | 0 | 0 | 0 | 1142 | 0 | 51 | 102 | 63 | 393 | 341 | 0 | 40 | 0 | 36 | 35 | 98 | 179 | 0 | 17 | 100 | 82 | 43 | 38 | 6 | 315 | 0 | 312 | 0 | 67 | 151 | 9 | 0 | 83 | 30 | 0 | 17 | 161 | 17 | 48 | 48 | 72 | 1 | 35.92 | 6 | 7334.03 | 930 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 80 | 1010 | 0 | 1229.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.48 | 104 | 0 | 0 | 60.92 | 178 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 5.54 | 0 | 0 | 35 | 21 | 0 | 0 | 0 | 0 | 4.8 | 190 | 0.59 | 0 | 170 | 110 | 180 | 0 | 302 | 1097 | 0 | 6444.51 | 13778.54 | 105.21
14:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 35 | 44 | 65 | 15 | 35 | 35 | 0 | 450 | 0 | 0 | 0 | 35 | 280 | 36 | 0 | 25 | 52 | 19 | 22 | 0 | 0 | 86 | 16 | 71 | 0 | 0 | 0 | 39 | 0 | 63 | 85 | 2.55 | 219 | 0 | 4 | 650 | 17 | 0 | 0 | 8 | 0 | 149 | 0 | 0 | 0 | 1160 | 2 | 51 | 100 | 63 | 350 | 320 | 0 | 39 | 0 | 36 | 34 | 98 | 177 | 0 | 17 | 100 | 88 | 43 | 57 | 31 | 310 | 0 | 314 | 0 | 66 | 149 | 9 | 0 | 83 | 30 | 0 | 17 | 161 | 17 | 48 | 48 | 71 | 2 | 11.08 | 6 | 7176.63 | 931 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 1042 | 0 | 1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.54 | 91 | 0 | 0 | 51.66 | 173 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 4.5 | 0 | 0 | 35 | 19 | 0 | 0 | 0 | 0 | 4.8 | 136 | 0.53 | 0 | 170 | 110 | 220 | 0 | 303 | 1050 | 0 | 6394.03 | 13570.66 | 105.2
15:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 19 | 17 | 35 | 44 | 65 | 15 | 35 | 54 | 0 | 450 | 0 | 0 | 0 | 35 | 319 | 94 | 0 | 19 | 35 | 19 | 22 | 0 | 0 | 87 | 16 | 72 | 0 | 6 | 0 | 38 | 0 | 50 | 86 | 1.85 | 219 | 0 | 2 | 650 | 17 | 0 | 0 | 8 | 0 | 149 | 0 | 0 | 0 | 1160 | 1 | 51 | 102 | 66 | 393 | 338 | 0 | 41 | 0 | 36 | 35 | 98 | 185 | 0 | 17 | 110 | 88 | 43 | 42 | 33 | 320 | 0 | 313 | 0 | 66 | 154 | 9 | 0 | 83 | 30 | 0 | 17 | 161 | 32 | 48 | 48 | 73 | 1 | 23.59 | 6 | 7378.44 | 930 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 1057 | 0 | 1263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.54 | 68 | 0 | 0 | 39.37 | 175 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 3.41 | 0 | 0 | 50 | 10 | 0 | 0 | 0 | 0 | 3.8 | 94 | 0.37 | 0 | 170 | 110 | 220 | 0 | 301 | 1080 | 0 | 6367.49 | 13745.93 | 105.19
16:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35.5 | 17 | 35 | 46 | 65 | 15 | 35 | 72 | 0 | 450 | 0 | 0 | 0 | 35 | 325 | 96 | 0 | 10 | 35 | 19 | 22 | 0 | 0 | 90 | 16 | 73 | 0 | 5 | 0 | 37 | 0 | 75 | 88 | 0.86 | 218 | 0 | 4 | 650 | 17 | 0 | 0 | 8 | 0 | 149 | 0 | 0 | 0 | 1115 | 0 | 51 | 102 | 63 | 393 | 334 | 0 | 40 | 0 | 36 | 34 | 99 | 180 | 1 | 17 | 88 | 86 | 43 | 9 | 40 | 315 | 0 | 313 | 0 | 66 | 148 | 9 | 0 | 83 | 30 | 0 | 17 | 161 | 35 | 53 | 48 | 72 | 0 | 6.12 | 6 | 7307.48 | 931 | 366 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 1078 | 0 | 1232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.96 | 35 | 0 | 0 | 18.71 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.63 | 0 | 0 | 50 | 5 | 0 | 0 | 0 | 0 | 1.9 | 52 | 0.18 | 0 | 180 | 110 | 220 | 0 | 314 | 1108 | 0 | 6379.38 | 13686.86 | 105.18
17:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 47 | 17 | 37 | 45 | 65 | 15 | 35 | 72 | 0 | 350 | 0 | 0 | 0 | 35 | 315 | 36 | 0 | 1 | 35 | 21.5 | 22 | 0 | 0 | 91 | 16 | 79 | 0 | 0 | 44 | 51 | 1 | 75 | 88 | 0.04 | 219 | 0 | 12 | 650 | 35 | 0 | 0 | 8 | 0 | 149 | 0 | 0 | 0 | 1138 | 0 | 51 | 45 | 63 | 360 | 320 | 0 | 38 | 0 | 36 | 34 | 100 | 178 | 6 | 17 | 75 | 82 | 43 | 2 | 40 | 315 | 0 | 313 | 0 | 66 | 151 | 9 | 0 | 52 | 28 | 0 | 17 | 161 | 35 | 58 | 48 | 72 | 0 | 0.47 | 6 | 7096.01 | 930 | 334 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 1116 | 0 | 1221 | 0 | 40 | 0 | 0 | 30 | 0 | 0 | 0 | 8 | 1.79 | 5 | 0 | 0 | 2.06 | 177 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0.16 | 0 | 0 | 50 | 1 | 34 | 0 | 0 | 0 | 0.3 | 6 | 0.02 | 1 | 180 | 110 | 220 | 0 | 349 | 1130 | 0 | 6342.33 | 13438.34 | 105.17
18:00 | 0 | 68 | 24 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 54 | 35 | 53 | 140 | 130 | 15 | 35 | 144 | 0 | 450 | 0 | 0 | 0 | 55 | 328 | 97 | 0 | 0 | 142 | 21.5 | 22 | 0 | 0 | 90 | 16 | 88 | 0 | 0 | 50 | 53 | 35 | 75 | 92 | 0 | 219 | 0 | 16 | 650 | 160 | 0 | 0 | 8 | 0 | 149 | 0 | 0 | 0 | 1186 | 0 | 51 | 90 | 63 | 393 | 342 | 0 | 41 | 0 | 33 | 48 | 101 | 178 | 8 | 17 | 98 | 90 | 43 | 0 | 40 | 315 | 0 | 313 | 0 | 66 | 147 | 9 | 0 | 83 | 30 | 0 | 17 | 161 | 22 | 48 | 48 | 72 | 0 | 0 | 0 | 8076.5 | 931 | 365 | 0 | 23 | 35 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1218 | 0 | 1432 | 0 | 47 | 0 | 10 | 46 | 0 | 95 | 15 | 52.2 | 0 | 0 | 18 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 112 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 180 | 110 | 220 | 0 | 464 | 1160 | 9 | 7290.2 | 15366.7 | 105.16
19:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 54 | 35 | 62 | 140 | 130 | 15 | 55 | 144 | 0 | 450 | 0 | 0 | 0 | 55 | 328 | 97 | 0 | 0 | 142 | 21.5 | 22 | 0 | 0 | 85 | 16 | 99 | 0 | 0 | 50 | 69 | 35 | 75 | 100 | 0 | 220 | 0 | 20 | 650 | 160 | 0 | 0 | 16 | 0 | 149 | 0 | 0 | 0 | 1134 | 0 | 51 | 112 | 63 | 340 | 351 | 0 | 42 | 0 | 34 | 70 | 101 | 170 | 0 | 17 | 95 | 90 | 43 | 0 | 40 | 305 | 0 | 312 | 0 | 66 | 146 | 0 | 0 | 83 | 30 | 0 | 17 | 161 | 17 | 58 | 47 | 73 | 0 | 0 | 0 | 8104.5 | 930 | 360 | 0 | 41 | 63 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1148 | 0 | 1462 | 0 | 47 | 0 | 35 | 111 | 0 | 95 | 35 | 52.2 | 0 | 0 | 18 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 180 | 110 | 220 | 0 | 408 | 1202 | 9 | 7317.2 | 15421.7 | 105.15
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 47 | 35 | 71 | 140 | 130 | 15 | 55 | 140 | 0 | 450 | 0 | 0 | 0 | 55 | 328 | 97 | 0 | 0 | 142 | 21.5 | 22 | 0 | 0 | 85 | 16 | 105 | 0 | 0 | 50 | 69 | 35 | 75 | 100 | 0 | 220 | 0 | 24 | 650 | 142 | 0 | 0 | 17 | 0 | 149 | 0 | 0 | 0 | 1157 | 0 | 51 | 123 | 63 | 340 | 350 | 0 | 42 | 0 | 37 | 80 | 101 | 170 | 0 | 17 | 74 | 86 | 43 | 0 | 40 | 310 | 0 | 312 | 0 | 66 | 139 | 0 | 0 | 83 | 30 | 0 | 17 | 161 | 17 | 49 | 47 | 73 | 0 | 0 | 0 | 8096.5 | 930 | 360 | 0 | 36 | 55 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 0 | 1465 | 0 | 47 | 0 | 35 | 113 | 0 | 95 | 38 | 52.2 | 0 | 0 | 18 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 180 | 110 | 220 | 0 | 401 | 1200 | 9 | 7278.2 | 15374.7
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 46.7 | 35 | 71 | 140 | 130 | 15 | 55 | 137 | 0 | 450 | 0 | 0 | 0 | 55 | 330 | 97 | 0 | 0 | 142 | 21.5 | 22 | 0 | 0 | 84 | 16 | 105 | 0 | 0 | 50 | 68 | 35 | 88 | 100 | 0 | 221 | 0 | 28 | 650 | 135 | 0 | 0 | 17 | 0 | 149 | 0 | 0 | 0 | 1134 | 0 | 51 | 123 | 63 | 340 | 353 | 0 | 42 | 0 | 37 | 81 | 101 | 136 | 0 | 17 | 52 | 88 | 43 | 0 | 40 | 305 | 0 | 312 | 0 | 67 | 139 | 0 | 0 | 83 | 30 | 0 | 17 | 161 | 17 | 49 | 47 | 73 | 0 | 0 | 0 | 8026.2 | 929 | 360 | 0 | 36 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1147 | 0 | 1466 | 0 | 47 | 0 | 35 | 113 | 0 | 95 | 38 | 52.2 | 0 | 0 | 18 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 180 | 110 | 220 | 0 | 400 | 1205 | 9 | 7295.2 | 15321.4 | 105.14
21:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 42.8 | 35 | 71 | 140 | 130 | 15 | 35 | 134 | 0 | 450 | 0 | 0 | 0 | 35 | 300 | 36 | 0 | 0 | 142 | 21.5 | 22 | 0 | 0 | 85 | 16 | 104 | 0 | 3 | 50 | 68 | 35 | 88 | 100 | 0 | 222 | 0 | 32 | 650 | 72 | 0 | 0 | 17 | 0 | 148 | 0 | 0 | 0 | 1160 | 0 | 51 | 128 | 63 | 340 | 351 | 0 | 43 | 0 | 37 | 80 | 102 | 129 | 0 | 17 | 49 | 82 | 43 | 0 | 40 | 310 | 0 | 312 | 0 | 67 | 143 | 8 | 0 | 83 | 30 | 0 | 17 | 160 | 17 | 48 | 48 | 73 | 0 | 0 | 0 | 7864.3 | 920 | 359 | 0 | 36 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1146 | 0 | 1469 | 0 | 47 | 0 | 35 | 113 | 0 | 95 | 38 | 52.2 | 0 | 0 | 18 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 180 | 110 | 220 | 0 | 353 | 1226 | 9 | 7288.2 | 15152.5 | 105.13
22:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 17.5 | 17 | 71 | 47 | 130 | 15 | 35 | 115 | 0 | 450 | 0 | 0 | 0 | 17 | 330 | 37 | 0 | 0 | 142 | 21.5 | 22 | 0 | 0 | 86 | 16 | 94 | 0 | 2 | 50 | 68 | 35 | 88 | 100 | 0 | 222 | 0 | 32 | 650 | 17 | 0 | 0 | 17 | 0 | 148 | 0 | 0 | 0 | 1155 | 0 | 51 | 128 | 63 | 393 | 353 | 0 | 43 | 0 | 37 | 73 | 102 | 126 | 0 | 17 | 15 | 90 | 16 | 0 | 40 | 310 | 0 | 312 | 0 | 67 | 148 | 8 | 0 | 83 | 30 | 0 | 17 | 160 | 17 | 49 | 48 | 73 | 0 | 0 | 0 | 7650 | 920 | 362 | 0 | 37 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1143 | 0 | 1469 | 0 | 47 | 0 | 35 | 113 | 0 | 95 | 38 | 8 | 0 | 0 | 18 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 180 | 110 | 220 | 0 | 354 | 1215 | 9 | 7185 | 14835 | 105.12
23:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 17.5 | 17 | 56 | 47 | 130 | 15 | 35 | 108 | 0 | 450 | 0 | 0 | 0 | 17 | 330 | 99 | 0 | 0 | 35 | 21.5 | 22 | 0 | 0 | 87 | 16 | 51 | 0 | 8 | 50 | 68 | 17 | 88 | 100 | 0 | 222 | 0 | 34 | 650 | 17 | 0 | 0 | 11 | 0 | 148 | 0 | 0 | 0 | 1137 | 0 | 51 | 130 | 63 | 395 | 353 | 0 | 43 | 0 | 38 | 37 | 103 | 126 | 0 | 17 | 0 | 94 | 16 | 0 | 40 | 315 | 0 | 312 | 0 | 67 | 154 | 8 | 0 | 83 | 30 | 0 | 17 | 160 | 17 | 49 | 48 | 101 | 0 | 0 | 0 | 7505 | 920 | 362 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1154 | 0 | 1465 | 0 | 47 | 0 | 35 | 113 | 0 | 95 | 37 | 0 | 0 | 0 | 18 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 50 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 180 | 110 | 220 | 0 | 353 | 1160 | 9 | 7020 | 14525 | 105.11
Total KWH | 0 | 1613760 | 354720 | 0 | 0 | 0 | 0 | 0 | 9842400 | 0 | 0 | 518040 | 506520 | 915840 | 1331040 | 1629905 | 292918 | 529250 | 1563840 | 0 | 10401500 | 0 | 0 | 0 | 530504 | 7629103 | 1034000 | 0 | 211938 | 1441200 | 490200 | 531360 | 0 | 0 | 1408855 | 270982 | 1034880 | 0 | 48000 | 553378 | 858528 | 278408 | 1699200 | 1861440 | 20684 | 5242115 | 0 | 490560 | 15672727.27 | 741018 | 0 | 0 | 182019.6 | 0 | 3455171 | 0 | 0 | 0 | 27823634 | 83970 | 1237516 | 1962109 | 1455273 | 9191000 | 8543500 | 0 | 998880 | 0 | 877752 | 1120320 | 2413102 | 3437760 | 21000 | 404040 | 1227780 | 1917120 | 589411 | 440136 | 542368 | 7591000 | 0 | 7850000 | 0 | 1579680 | 3656373 | 193272 | 0 | 1968000 | 715296 | 0 | 196000 | 3333280 | 484560 | 1195200 | 1154400 | 1947840 | 12500 | 248090 | 96720 | 171694885.87 | 22496727 | 8390880 | 0 | 165600 | 186240 | 912000 | 0 | 0 | 0 | 0 | 0 | 587520 | 26174540 | 0 | 31398280 | 0 | 332770 | 0 | 223008 | 914592 | 0 | 641920 | 191500 | 236410 | 409962 | 755390 | 154718 | 0 | 389248 | 4142091 | 0 | 0 | 0 | 0 | 0 | 8900581 | 0 | 34860 | 0 | 0 | 1259665 | 206348 | 1020768 | 0 | 0 | 0 | 38330.28 | 1152720 | 3900 | 198720 | 4189000 | 2635000 | 5373490 | 0 | 8480000 | 27482181.82 | 60000 | 159738960.1 | 331433845.97

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13590.93 | MW | 12:00 Hr. | Energy Generated |  |  | 331.4338 |  | MKWHr.
| Day Peak Demand |  |  | 13855.32 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.58 |  | MKWHr.
| Evening Peak Generation |  |  | 15421.7 | MW | 19:00 Hr. | Energy Demand |  |  | 335.0138 |  | MKWHr.
| Evening Peak Demand |  |  | 15510.7 | MW | 19:00 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 12304.45 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 860.1 |  | MMCFD
| Maximum Generation of the Day |  |  | 15421.7 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.6424 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 29.9286 | 0 | 11.2275 | 0 | 0 | 0.21194 | 0 | 0 | 41.368 | Gas | 117.4681 | Gas | 422533088.62
| Chattogram Zone |  |  | 3.9457 | 43.4964 | 8.8887 | 0 | 5.2421 | 0.10465 | 0 | 0.048 | 61.7256 | Coal | 109.8221 | Coal | 694809760.8583
| Cumilla Zone |  |  | 25.1211 | 0 | 8.9007 | 0 | 0 | 0.44014 | 1.9171 | 0 | 36.3791 | HFO | 37.5338 | HFO | 669511251.224
| Mymensingh Zone |  |  | 1.9478 | 0 | 2.9309 | 0 | 0 | 0.26059 | 0 | 0 | 5.1393 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.0829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.0829 | Hydro | 5.2421 | Hydro | 524211.5
| Khulna Zone |  |  | 8.3909 | 26.1745 | 0.35184 | 0 | 0 | 0.58752 | 23.4087 | 0 | 58.9135 | Solar | 4.5956 | Solar | 73065887.9748
| Barishal Zone |  |  | 8.0085 | 40.1512 | 0.25872 | 0 | 0 | 0.0039 | 0 | 0 | 48.4223 | Import | 56.7241 | Import | 340375430.97
| Rajshahi Zone |  |  | 13.0427 | 0 | 2.6949 | 0 | 0 | 1.5895 | 31.3983 | 0 | 48.7253 | Wind | 0.048 | Wind | 706080
| Rangpur Zone |  |  | 0 | 0 | 2.2804 | 0 | 0 | 1.3974 | 0 | 0 | 3.6778
| Total |  |  | 117.4681 | 109.8221 | 37.5338 | 0 | 5.2421 | 4.5956 | 56.7241 | 0.048 | 331.4338
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 422533088.62 |  | Hydro | 524211.5
|  |  |  | Coal | 694809760.8583 |  | Solar | 73065887.9748
|  |  |  | HFO | 669511251.224 |  | Import | 340375430.97
|  |  |  | HSD | 0 |  | Wind | 706080
[5 empty] | Total: | 220,15,25,711 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.4967 | Peak Hr Flow | 930.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 53773789.89 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.3983 | Peak Hr Flow | 1462.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2451 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.9171 | Peak Hr Flow | 90.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2790 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 55.8121 | Peak Hr Flow | 2482.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5375
|  |  |  | Chattogram |  | 0 |  | 1543
|  |  |  | Cumilla |  | 0 |  | 1513
|  |  |  | Mymensingh |  | 85 |  | 1157
|  |  |  | Sylhet |  | 0 |  | 657
|  |  |  | Khulna |  | 0 |  | 1738
|  |  |  | Barishal |  | 0 |  | 474
|  |  |  | Rajshahi |  | 0 |  | 1412
|  |  |  | Rangpur |  | 0 |  | 933
|  |  |  | Total |  | 85 |  | 14802
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:19 | 12:59 | Noapara 132/33kV S/S T-1 LT Scheduled S/D Due to For Annual Maintenance work.
| 08:20 | 12:59 | Noapara 132/33kV S/S T-1 HT Scheduled S/D Due to For Annual Maintenance work.
| 08:28 | 17:07 | Aminbazar 400/230/132kV S/S 132 kv Bus 01 Scheduled S/D Due to Annual Maintenance
| 08:30 | 16:45 | Bogura-Sirajganj 230 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end Due to Annual
Maintenance and from Sirajgonj 230 end Due to Annual Maintenance
| 08:40 |  | Saidpur 132/33kV S/S TR-2 (404T) LT Project Work S/D Due to Replacement of transformer
T-02 by a new one.
| 08:40 |  | Saidpur 132/33kV S/S TR-2 (404T) HT Project Work S/D Due to Replacement of transformer
T-02 by a new one.
| 08:40 |  | Savar 132/33kV S/S Main Bus-I Scheduled S/D Due to Annual maintenance
| 08:49 | 17:46 | Gopalganj 400/132kV S/S ATR-03 LT Scheduled S/D Due to Annual Maintenance
| 08:50 | 17:41 | Gopalganj 400/132kV S/S ATR-03 HT Scheduled S/D Due to Annual Maintenance
|  | 08:51 | Bhaluka 132/33kV S/S Sreepur Ckt- 01 is restored.
|  | 08:51 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-1 is restored.
| 09:18 | 16:10 | Panchagarh 132/33kV S/S 132KV Capacitor Bank Scheduled S/D Due to Annual Maintenance work
|  | 10:23 | Mirpur 132/33kV S/S T3 HT is restored.
| 12:00 |  | Day Peak Generation: 13585 MW.
| 12:23 | 14:52 | Shikalbaha 230/132kV S/S Interconnection-1 Scheduled S/D
| 12:35 | 13:37 | Saidpur 132/33kV S/S BUS A Project Work S/D Due to project work
| 12:35 | 13:37 | Saidpur 132/33kV S/S 132 kV BUS Coupler Project Work S/D Due to Project work.
|  | 12:51 | Hasnabad 230/132kV S/S AUTO TR-2 HT is restored.
|  | 12:54 | Hasnabad 230/132kV S/S AUTO TR-2 LT is restored.
|  | 12:55 | Jamalpur-Mymensingh 132kV Ckt-1 is restored.
| 12:56 | 20:41 | Hasnabad 230/132kV S/S AUTO TR-2 LT Forced S/D Due to 132 kv main Bus side D/S-221
R-Phase Finger Maintenance.
| 13:15 | 15:55 | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due to
Temperature maintenance work
| 13:17 | 20:41 | Hasnabad 230/132kV S/S AUTO TR-2 HT Forced S/D Due to 132 kv main Bus side D/S-221
R-Phase Finger Maintenance.
|  | 14:14 | Barishal 230/132kV S/S ATR-2 LT is restored.
|  | 14:16 | Barishal 230/132kV S/S ATR-2 HT is restored.
| 14:31 | 17:41 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT Scheduled S/D Due to 132 kv Reserve Bus D/S
Maintenance
| 14:31 | 17:41 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT Scheduled S/D Due to 132 kv Reserve Bus D/S
Maintenance
| 14:31 | 17:41 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Scheduled S/D Due to 132 kv Reserve Bus D/S
Maintenance
|  | 14:32 | Rampur 230/132/33 S/S TR-1 HT is restored.
| 14:40 | 16:19 | Tangail 132/33kV S/S Tr-4 LT Scheduled S/D Due to 33 kv shakhipur feeder CT Maintenance
| 14:44 | 16:18 | Tangail 132/33kV S/S Tr-4 HT Scheduled S/D Due to 33 kv shakhipur feeder CT Maintenance
|  | 14:46 | Rampur 230/132/33 S/S TR-1 LT is restored.
| 15:25 | 17:09 | Rahanpur 400/132kV S/S Rahanpur-Chowdala 132 KV Line Ckt-02 Scheduled S/D Due to As per
instruction of ALDC Bogura
| 15:25 | 17:10 | Rahanpur 132/33kV S/S Rahanpur-2 Project Work S/D Due to DS QB1 not working in remote.
CCCE technician fixing it.
| 15:45 | 17:28 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bhandaria 132/33kV end.
| 16:02 | 17:51 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to remove red hot T2 33 kv bus | [7 empty] | 10.0MW load
interrup.
| 16:04 | 17:50 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to remove red hot T2 33 kv bus | [7 empty] | 10.0MW load
interrup.
|  | 16:36 | Barguna 132/33kV S/S Transformer-2 HT is restored.
|  | 16:37 | Barguna 132/33kV S/S Transformer-2 LT is restored.
| 16:44 |  | Rooppur- Baghabari 230kV ckt-1 and 2 were switched ON.
|  | 16:53 | Chauddagram-Cumilla(S) 132 kV Ckt-1 is restored.
| 18:22 |  | Sathia- bera 132 KV ckt Synchronize
| 19:00 |  | Evening peak Generation is 15421 MW
| 01:25 | 01:30 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing O/C relays Due to Due to polashpur 33 | [7 empty] | 60.0MW load
|  |  | kV feeder WZPDCL | [7 empty] | interrup.
| 06:34 |  | Meghnaghat 230/132kV S/S Meghnaghat-SMPCL-02 Project Work S/D Due to Dismantling and
reinstallation work of dia-07
| 06:58 |  | Ashuganj-Ghorasal 132kV Ckt-1 Forced S/D from Ashuganj 230/132/33kV end Due to As per
instruction of NLDC
| 06:59 |  | Ashuganj-Ghorasal 132kV Ckt-2 Forced S/D from Ashuganj 230/132/33kV end Due to As per
instruction of NLDC
| 07:00 |  | Minimum Generation: 11572 MW.
| 07:04 |  | Ghorashal 230/132kV Tr-2 was shut down for scheduled maintenance.
| 07:10 |  | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Red Hot Maintenance. | [7 empty] | 55.0MW load
interrup.
| 07:12 |  | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Red Hot Maintenance. | [7 empty] | 55.0MW load
interrup.
| 07:20 |  | Saidpur 132/33kV S/S TR-3 (424T) LT Forced S/D Due to 33 kv side CT joint point Red hot. | [7 empty] | 12.0MW load
|  |  | Clamp replacement. | [7 empty] | interrup.
| 07:21 |  | Saidpur 132/33kV S/S TR-3 (424T) HT Forced S/D Due to CT clamp replacement | [7 empty] | 12.0MW load
interrup.
| 07:58 |  | Sikalbaha Gas 225 MW was shut down for changing the air intake filter of gas turbine.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 413 | 9842400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10401500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 292918 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 97 | 1034000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7629103 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 518040 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 140 | 1331040 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 529250 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 530504 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21.5 | 490200 | Partial Shutdown due to maintenance
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 531360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 354720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 130 | 1629905 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 62 | 915840 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1613760 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1563840 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 211938 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 506520 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1441200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2292.5 | 41368038
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 16 | 182019.6 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 83970 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5242115 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 149 | 3455171 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 69 | 858528 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 553378 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 75 | 1699200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 490560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 99 | 1034880 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20684 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 270982 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 35 | 278408 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1861440 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 85 | 1408855 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 160 | 741018 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1134 | 27823634 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 48000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15672727.27 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2878 | 61725569.87
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 351 | 8543500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 340 | 9191000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 877752 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 42 | 998880 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 63 | 1455273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1237516 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 112 | 1962109 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 40 | 542368 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 101 | 2413102 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 3437760 | -
| Import (Tripura) |  | Import | 0 | 160 | 90 | 1917120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 589411 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 404040 | Schedule Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 95 | 1227780 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 21000 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 70 | 1120320 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 440136 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1619 | 36379067
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 73 | 1947840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 47 | 1154400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 1195200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 248090 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 96720 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 484560 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 195 | 5139310
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 66 | 1579680 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 146 | 3656373 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 715296 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1968000 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 161 | 3333280 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 196000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 193272 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7591000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 312 | 7850000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2325 | 1120 | 27082901
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 930 | 22496727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 41 | 165600 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 63 | 186240 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 360 | 8390880 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 587520 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1148 | 26174540 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2580 | 58913507
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 408 | 8480000 | On Test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 198720 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2635000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1202 | 27482181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5373490 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 9 | 60000 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 180 | 4189000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3900 | -
Barishal Area Total |  |  |  |  | 2858 | 2161 | 48422291.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 409962 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 332770 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 191500 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 166 | 4142091 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 333 | 8900581 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 18 | 154718 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 236410 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 641920 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 111 | 914592 | Fuel shortage as BPDB payment not done in time
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 223008 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34860 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1462 | 31398280 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 389248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 755390 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2354.2 | 48725330
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1020768 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38330.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1259665 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 206348 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1152720 | -
Rangpur Area Total |  |  |  |  | 950 | 222 | 3677831.28
Eastern Grid Total |  |  |  |  | 17383.852 | 8104.5 | 171694885.87
Western Grid Total |  |  |  |  | 10980.24 | 7317.2 | 159738960.1
National Grid Total |  |  |  |  | 28364.092 | 15421.7 | 331433845.97
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10159.58 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4556.5 | MW
i) Dhaka area |  |  | 5374.85 |  | MW | i) Khulna area |  |  |  | 1738 | MW
ii) Chattogram area |  |  | 1543 |  | MW | ii) Barishal area |  |  |  | 473.5 | MW
iii) Cumilla area |  |  | 1512.73 |  | MW | iii) Rajshahi area |  |  |  | 1412 | MW
iv) Mymensingh area |  |  | 1072 |  | MW | iv) Rangpur area |  |  |  | 933 | MW
v) Sylhet area |  |  | 657 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14716.08 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 89 | 18:00 | 133 | Niamatpur | 78 | 18:00
2 | AKSML | 135 | 23:00 | 68 | Ishurdi | 76 | 18:00 | 134 | Noapara | 45 | 18:30
3 | Aftabnagar | 42 | 13:00 | 69 | Jaldhaka | 74 | 18:30 | 135 | PHP | 7 | 16:00
4 | Agargaon | 139 | 13:00 | 70 | Jamalpur | 109 | 07:00 | 136 | Pabna | 96 | 18:30
5 | Agrabad | 132 | 10:00 | 71 | Jashore | 138 | 18:00 | 137 | Palashbari | 118 | 18:30
6 | Amnura | 36 | 18:30 | 72 | Jhenaidah | 130 | 18:00 | 138 | Panchagarh | 58 | 18:00
7 | Ashuganj | 100 | 00:00 | 73 | Joydebpur | 138 | 19:30 | 139 | Patiya | 10 | 00:00
8 | BSRM | 201 | 20:00 | 74 | Joypurhat | 59 | 00:00 | 140 | Patuakhali | 70.5 | 22:00
9 | Bagerhat | 89 | 18:00 | 75 | Juldah | 19.5 | 00:00 | 141 | Payra | 36 | 23:00
10 | Bajitpur | 70 | 22:00 | 76 | KSRM | 16 | 11:00 | 142 | Postogola | 70 | 00:00
11 | Bakulia | 94 | 15:00 | 77 | Kabirpur | 244 | 18:00 | 143 | Purbachal | 22 | 00:00
12 | Banani | 56 | 13:00 | 78 | Kachua | 97 | 18:00 | 144 | Purbasadipur | 115 | 18:30
13 | Bangabhaban | 27 | 10:00 | 79 | Kallyanpur | 105 | 22:00 | 145 | Rahanpur | 33 | 20:00
14 | Barapukuria | 60 | 18:30 | 80 | Kalurghat | 54 | 12:00 | 146 | Rahim | 31 | 22:00
15 | Barguna | 22 | 21:00 | 81 | Kamrangirchar | 81 | 17:00 | 147 | Rajbari | 78 | 18:00
16 | Barishal | 117 | 18:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 120 | 18:00
17 | Barishal-230 | 98 | 18:30 | 83 | Kasba | 38 | 19:30 | 149 | Rajshahi | 104 | 00:00
18 | Baroaulia | 73 | 20:00 | 84 | Kazla | 103 | 13:00 | 150 | Rajshahi-230 | 87 | 13:00
19 | Baroirhat | 67 | 18:00 | 85 | Keranigonj | 88 | 19:00 | 151 | Ramganj | 120 | 23:00
20 | Bashundhara | 211 | 13:00 | 86 | Khagrachori | 34 | 18:00 | 152 | Rampur | 59 | 00:00
21 | BashundharaCement | 14 | 19:30 | 87 | Khulna | 65 | 13:00 | 153 | Rangamati | 18 | 18:00
22 | Beanibazar | 84 | 18:00 | 88 | Khulshi | 199 | 19:30 | 154 | Rangpur | 142 | 18:00
23 | Benapole | 56 | 12:00 | 89 | Kishoreganj | 126 | 20:00 | 155 | Ruppur | 8.2 | 11:00
24 | Bhaluka | 143 | 19:00 | 90 | Kodda | 301 | 18:00 | 156 | SSM | 7 | 22:00
25 | Bhandaria | 57 | 21:00 | 91 | Kulaura | 56 | 18:00 | 157 | Saidpur | 110 | 18:00
26 | Bhangura | 41 | 18:00 | 92 | Kurigram | 62 | 18:00 | 158 | Satkhira | 122 | 21:00
27 | Bheramara(GK) | 62 | 18:00 | 93 | Kushtia | 140 | 18:30 | 159 | Satmasjid | 107 | 13:00
28 | Bhulta | 216 | 23:00 | 94 | Laksam | 37 | 01:00 | 160 | Savar | 224 | 18:00
29 | Bog-Sherpur | 64 | 18:00 | 95 | Lakshmipur | 33 | 00:00 | 161 | SevenRings | 5.43 | 17:00
30 | Bogura | 170 | 19:00 | 96 | Lalbag | 70 | 11:00 | 162 | ShahCement | 21 | 00:00
31 | Borhanuddin | 95 | 00:00 | 97 | Lalmonirhat | 56 | 18:30 | 163 | Shahjadpur | 81 | 18:00
32 | Brahmanbaria | 138 | 20:00 | 98 | MI_Cement | 16.3 | 02:00 | 164 | Shahjibazar | 134 | 21:00
33 | Cantonment | 170 | 13:00 | 99 | Madanganj | 51 | 21:00 | 165 | Shahmirpur | 51 | 00:00
34 | Chandina | 17.17 | 00:00 | 100 | Madaripur | 107 | 19:30 | 166 | Shariatpur | 88 | 21:00
35 | Chandpur | 84 | 19:30 | 101 | Madartek | 96 | 00:00 | 167 | Sherpur | 120 | 23:00
36 | Chandraghona | 38 | 18:30 | 102 | Madunaghat | 57 | 00:00 | 168 | Shikalbaha | 32 | 14:00
37 | Chapai | 66 | 19:30 | 103 | Magura | 62 | 18:30 | 169 | Shitalakhya | 82.8 | 15:00
38 | Charsaidpur | 37 | 11:00 | 104 | Mahasthangarh | 72 | 00:00 | 170 | Sholosohor | 49 | 10:00
39 | Chauddagram | 75 | 01:00 | 105 | Maijdee | 33 | 21:00 | 171 | Shyampur | 144 | 00:00
40 | Chhatak | 39 | 19:30 | 106 | Manikganj | 122 | 18:00 | 172 | Siddhirganj | 126 | 16:00
41 | Chowmuhani | 173 | 21:00 | 107 | Maniknagar | 66 | 13:00 | 173 | Sirajganj | 102 | 18:00
42 | Chuadanga | 109 | 18:00 | 108 | Matarbari | 55 | 21:00 | 174 | Sonargaon | 118 | 19:00
43 | Coxsbazar | 141 | 12:00 | 109 | Matuail | 75 | 11:00 | 175 | Sreemongol | 87 | 19:00
44 | Cumilla(N) | 152 | 19:00 | 110 | Metrorail_Motijheel | 32 | 18:30 | 176 | Sreepur | 111 | 19:30
45 | Cumilla(S) | 170 | 18:00 | 111 | Metrorail_Uttara | 6 | 11:00 | 177 | Srinagar | 47.9 | 21:00
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 128 | 14:00 | 178 | Sunamganj | 65 | 19:30
47 | Daudkandi | 156 | 19:30 | 113 | Mirpur | 125.5 | 18:30 | 179 | Sylhet | 54 | 18:30
48 | DhakaUniversity | 100 | 13:00 | 114 | Mirsorai | 12 | 18:30 | 180 | Sylhet-132 | 142 | 16:00
49 | Dhamrai | 128 | 18:00 | 115 | Mirzapur | 38 | 19:00 | 181 | TK | 23 | 00:00
50 | Dhanmondi | 131 | 12:00 | 116 | Mithapukur | 58 | 18:00 | 182 | Tangail | 158 | 11:00
51 | Dohazari | 107 | 20:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 22 | 18:30
52 | Faridpur | 159 | 18:30 | 118 | Mogbazar | 103.6 | 13:00 | 184 | Thakurgaon | 95 | 18:30
53 | Fatullah | 119 | 15:00 | 119 | Mongla | 45 | 17:00 | 185 | Tongi | 138 | 15:00
54 | Fenchuganj | 44 | 18:00 | 120 | Motijheel | 50 | 14:00 | 186 | Ullahpara | 35 | 18:00
55 | Feni | 128 | 18:00 | 121 | Muktagacha | 32 | 07:00 | 187 | Ullon | 70 | 00:00
56 | GPH | 8 | 18:30 | 122 | Munshiganj | 113 | 16:00 | 188 | Uttara | 97 | 13:00
57 | Ghatail | 68 | 07:00 | 123 | Muradnagar | 45 | 19:30 | 189 | UttaraNew | 60 | 01:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 192 | 21:00 | 190 | Zigatola | 74 | 12:00
59 | Ghorashal-230 | 101 | 02:00 | 125 | Naogaon | 121 | 00:00
60 | Goalpara | 33 | 00:00 | 126 | Narail | 57 | 18:30
61 | Gollamari | 100 | 18:30 | 127 | Narinda | 72 | 13:00
62 | Gopalganj | 107 | 18:30 | 128 | Narshingdi | 176 | 02:00
63 | Gulshan | 138 | 13:00 | 129 | Natore | 140 | 18:00
64 | Halishahar | 78 | 11:00 | 130 | Nawabganj | 45.2 | 21:00
65 | HaripurSBU | 155 | 17:00 | 131 | Netrakona | 149 | 18:00
66 | Hasnabad | 98 | 18:00 | 132 | New | 58.8 | 11:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14387.78 | 299 |  | 14700.24
1:00 | 14063.24 | 180 |  | 14251.24
2:00 | 13618.85 | 126 |  | 13750.85
3:00 | 13215.57 | 129 |  | 13350.57
4:00 | 12885.9 | 110 |  | 13000.9
5:00 | 12540.62 | 96 |  | 12640.62
6:00 | 12304.45 | 64 |  | 12371.45
7:00 | 12515.17 | 76 |  | 12594.17
8:00 | 12447.94 | 95 |  | 12547.22
9:00 | 12564.69 | 88 |  | 12656.65
10:00 | 12783.54 | 116 |  | 12904.76
11:00 | 13337.5 | 159 |  | 13503.66
12:00 | 13590.93 | 253 |  | 13855.32
13:00 | 13778.54 | 360 |  | 14154.74
14:00 | 13570.66 | 356 |  | 13942.66
15:00 | 13745.93 | 294 |  | 14052.93
16:00 | 13686.86 | 160 |  | 13853.86
17:00 | 13438.34 | 157 |  | 13602.34
18:00 | 15366.7 | 109 |  | 15480.7
19:00 | 15421.7 | 85 |  | 15510.7
19:30 | 15374.7 | 73 |  | 15450.7
20:00 | 15321.4 | 57 |  | 15381.4
21:00 | 15152.5 | 47 |  | 15201.5
22:00 | 14835 | 63 |  | 14900.84
23:00 | 14525 | 101 |  | 14630.55
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7219.5 | 7168.28 | 14387.78 | DAILY GENERATION CURVE
00:30 | 7191.5 | 7034.01 | 14225.51
01:00 | 7163.5 | 6899.74 | 14063.24 | 23-10-2025
01:30 | 7163 | 6678.045 | 13841.045
02:00 | 7162.5 | 6456.35 | 13618.85
02:30 | 6979 | 6438.21 | 13417.21
03:00 | 6795.5 | 6420.07 | 13215.57
03:30 | 6698.5 | 6352.235 | 13050.735
04:00 | 6601.5 | 6284.4 | 12885.9
04:30 | 6498 | 6215.26 | 12713.26
05:00 | 6394.5 | 6146.12 | 12540.62
05:30 | 6373 | 6049.535 | 12422.535
06:00 | 6351.5 | 5952.95 | 12304.45
06:30 | 6356.55 | 6053.26 | 12409.81
07:00 | 6361.6 | 6153.57 | 12515.17
07:30 | 6326.405 | 6155.15 | 12481.555
08:00 | 6291.21 | 6156.73 | 12447.94
08:30 | 6292.785 | 6213.53 | 12506.315
09:00 | 6294.36 | 6270.33 | 12564.69
09:30 | 6464.145 | 6209.97 | 12674.115
10:00 | 6633.93 | 6149.61 | 12783.54
10:30 | 6817.61 | 6242.91 | 13060.52
11:00 | 7001.29 | 6336.21 | 13337.5
11:30 | 7124.56 | 6339.655 | 13464.215
12:00 | 7247.83 | 6343.1 | 13590.93
12:30 | 7290.93 | 6393.805 | 13684.735
13:00 | 7334.03 | 6444.51 | 13778.54
13:30 | 7255.33 | 6419.27 | 13674.6
14:00 | 7176.63 | 6394.03 | 13570.66
14:30 | 7277.535 | 6380.76 | 13658.295
15:00 | 7378.44 | 6367.49 | 13745.93
15:30 | 7342.96 | 6373.435 | 13716.395
16:00 | 7307.48 | 6379.38 | 13686.86
16:30 | 7201.745 | 6360.855 | 13562.6
17:00 | 7096.01 | 6342.33 | 13438.34
17:30 | 7586.255 | 6816.265 | 14402.52
18:00 | 8076.5 | 7290.2 | 15366.7
18:30 | 8090.5 | 7303.7 | 15394.2
19:00 | 8104.5 | 7317.2 | 15421.7
19:30 | 8096.5 | 7278.2 | 15374.7
20:00 | 8026.2 | 7295.2 | 15321.4
20:30 | 7945.25 | 7291.7 | 15236.95 |  | Executive Engineer
21:00 | 7864.3 | 7288.2 | 15152.5 |  | Network Operation Division
21:30 | 7757.15 | 7236.6 | 14993.75
22:00 | 7650 | 7185 | 14835
22:30 | 7577.5 | 7102.5 | 14680
23:00 | 7505 | 7020 | 14525

## En-Curve
QF-LDC-12
Date | 23-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3449 | 1454.5 | 929 | 38 | 92 | 1468.28 | 222 | 4854 | 0 | 461 | 1420 | 0 | 0 | 0 | 299 | DAILY ENERGY CURVE
00:30 | 3414 | 1466 | 929.5 | 38 | 87 | 1463.01 | 221.5 | 4796 | 0 | 379 | 1431.5 | 0 | 0 | 0 | 239.5 | 23-10-2025
01:00 | 3379 | 1477.5 | 930 | 38 | 82 | 1457.74 | 221 | 4738 | 0 | 297 | 1443 | 0 | 0 | 0 | 180
01:30 | 3378.5 | 1487 | 930 | 38 | 81 | 1460.045 | 220 | 4692 | 0 | 273 | 1281.5 | 0 | 0 | 0 | 153 | Energy Generated | 331.4338 |  | MKWHr
02:00 | 3378 | 1496.5 | 930 | 38 | 80 | 1462.35 | 219 | 4646 | 0 | 249 | 1120 | 0 | 0 | 0 | 126 | Energy not Served | 3.58 |  | MKWHr
02:30 | 3392.5 | 1477.5 | 930.5 | 38 | 78 | 1463.21 | 219 | 4623.5 | 0 | 227 | 968 | 0 | 0 | 0 | 127.5 | Total Energy Requirement | 335.0138 |  | MKWHr
03:00 | 3407 | 1458.5 | 931 | 38 | 76 | 1464.07 | 219 | 4601 | 0 | 205 | 816 | 0 | 0 | 0 | 129
03:30 | 3415 | 1458.5 | 930.5 | 38 | 75 | 1396.235 | 219 | 4594.5 | 0 | 156 | 768 | 0 | 0 | 0 | 119.5
04:00 | 3423 | 1458.5 | 930 | 38 | 74 | 1328.4 | 219 | 4588 | 0 | 107 | 720 | 0 | 0 | 0 | 110
04:30 | 3422 | 1460 | 930 | 38 | 74 | 1323.26 | 219 | 4543.5 | 0 | 107 | 596.5 | 0 | 0 | 0 | 103
05:00 | 3421 | 1461.5 | 930 | 38 | 74 | 1318.12 | 219 | 4499 | 0 | 107 | 473 | 0 | 0 | 0 | 96
05:30 | 3426 | 1464 | 930 | 38 | 75 | 1274.535 | 219 | 4430 | 0 | 107 | 459 | 0 | 0 | 0 | 80
06:00 | 3431 | 1466.5 | 930 | 38 | 76 | 1230.95 | 219 | 4361 | 0 | 107 | 445 | 0 | 0 | 0 | 64
06:30 | 3457.5 | 1474.5 | 930 | 38 | 74 | 1229.865 | 219.5 | 4371.5 | 57.445 | 107 | 450 | 0 | 0 | 0.5 | 70
07:00 | 3484 | 1482.5 | 930 | 38 | 72 | 1228.78 | 220 | 4382 | 114.89 | 107 | 455 | 0 | 0 | 1 | 76
07:30 | 3363 | 1463 | 930 | 38 | 72 | 1205.48 | 220 | 4394 | 217.575 | 133.5 | 444.5 | 0 | 0 | 0.5 | 85.5
08:00 | 3242 | 1443.5 | 930 | 38 | 72 | 1182.18 | 220 | 4406 | 320.26 | 160 | 434 | 0 | 0 | 0 | 95
08:30 | 3202 | 1440.75 | 930.5 | 38 | 68 | 1182.465 | 220 | 4415.5 | 412.1 | 167.5 | 429 | 0 | 0 | 0.5 | 91.5
09:00 | 3162 | 1438 | 931 | 38 | 64 | 1182.75 | 220 | 4425 | 503.94 | 175 | 424 | 0 | 0 | 1 | 88
09:30 | 3229 | 1441.5 | 931 | 38 | 64 | 1111.23 | 220.5 | 4392 | 548.885 | 175 | 522.5 | 0 | 0 | 0.5 | 102
10:00 | 3296 | 1445 | 931 | 38 | 64 | 1039.71 | 221 | 4359 | 593.83 | 175 | 621 | 0 | 0 | 0 | 116
10:30 | 3371.5 | 1451.5 | 931 | 38 | 68 | 1025.965 | 221 | 4343.5 | 626.055 | 181.5 | 802.5 | 0 | 0 | 0 | 137.5
11:00 | 3447 | 1458 | 931 | 38 | 72 | 1012.22 | 221 | 4328 | 658.28 | 188 | 984 | 0 | 0 | 0 | 159
11:30 | 3501.5 | 1452.25 | 931 | 38 | 75 | 1027.655 | 221 | 4335.5 | 637.81 | 196 | 1048.5 | 0 | 0 | 0 | 206
12:00 | 3556 | 1446.5 | 931 | 38 | 78 | 1043.09 | 221 | 4343 | 617.34 | 204 | 1113 | 0 | 0 | 0 | 253
12:30 | 3489 | 1428.25 | 930.5 | 38 | 80 | 1136.135 | 221 | 4357 | 624.35 | 219.5 | 1161 | 0 | 0 | 0 | 306.5
13:00 | 3422 | 1410 | 930 | 38 | 82 | 1229.18 | 221 | 4371 | 631.36 | 235 | 1209 | 0 | 0 | 0 | 360
13:30 | 3352 | 1423 | 930.5 | 38 | 85 | 1228.09 | 220 | 4373 | 578.01 | 238.5 | 1208.5 | 0 | 0 | 0 | 358
14:00 | 3282 | 1436 | 931 | 38 | 88 | 1227 | 219 | 4375 | 524.66 | 242 | 1208 | 0 | 0 | 0 | 356
14:30 | 3361.5 | 1445 | 930.5 | 38 | 88 | 1245 | 219 | 4396.5 | 458.795 | 234 | 1239 | 0 | 0 | 3 | 325
15:00 | 3441 | 1454 | 930 | 38 | 88 | 1263 | 219 | 4418 | 392.93 | 226 | 1270 | 0 | 0 | 6 | 294
15:30 | 3500.5 | 1447.5 | 930.5 | 38 | 87 | 1247.5 | 218.5 | 4431.5 | 290.645 | 226 | 1293.25 | 0 | 0 | 5.5 | 227
16:00 | 3560 | 1441 | 931 | 38 | 86 | 1232 | 218 | 4445 | 188.36 | 226 | 1316.5 | 0 | 0 | 5 | 160
16:30 | 3454.5 | 1381.25 | 930.5 | 38 | 84 | 1226.5 | 218.5 | 4504 | 106.6 | 274.5 | 1341.75 | 0 | 0 | 2.5 | 158.5
17:00 | 3349 | 1321.5 | 930 | 38 | 82 | 1221 | 219 | 4563 | 24.84 | 323 | 1367 | 0 | 0 | 0 | 157
17:30 | 3456.5 | 1388.5 | 930.5 | 38 | 86 | 1326.5 | 219 | 4710.5 | 12.42 | 536.5 | 1698.1 | 0 | 0 | 0 | 133
18:00 | 3564 | 1455.5 | 931 | 38 | 90 | 1432 | 219 | 4858 | 0 | 750 | 2029.2 | 0 | 0 | 0 | 109
18:30 | 3502.5 | 1448 | 930.5 | 38 | 90 | 1447 | 219.5 | 4790 | 0 | 809.5 | 2119.2 | 0 | 0 | 0 | 97
19:00 | 3441 | 1440.5 | 930 | 38 | 90 | 1462 | 220 | 4722 | 0 | 869 | 2209.2 | 0 | 0 | 0 | 85
19:30 | 3443 | 1442.5 | 930 | 38 | 86 | 1465 | 220 | 4710 | 0 | 851 | 2189.2 | 0 | 0 | 0 | 73
20:00 | 3440 | 1441.5 | 929 | 38 | 88 | 1466 | 221 | 4716 | 0 | 845 | 2136.9 | 0 | 0 | 0 | 57
20:30 | 3406.5 | 1452.5 | 924.5 | 38 | 85 | 1467.5 | 221.5 | 4715.5 | 0 | 845 | 2079.45 | 0 | 0 | 1.5 | 52
21:00 | 3373 | 1463.5 | 920 | 38 | 82 | 1469 | 222 | 4715 | 0 | 845 | 2022 | 0 | 0 | 3 | 47
21:30 | 3417 | 1466 | 920 | 38 | 86 | 1469 | 222 | 4706 | 0 | 774 | 1893.25 | 0 | 0 | 2.5 | 55
22:00 | 3461 | 1468.5 | 920 | 38 | 90 | 1469 | 222 | 4697 | 0 | 703 | 1764.5 | 0 | 0 | 2 | 63
22:30 | 3513.5 | 1475 | 920 | 38 | 92 | 1467 | 222 | 4665.5 | 0 | 630.5 | 1651.5 | 0 | 0 | 5 | 82
23:00 | 3566 | 1481.5 | 920 | 38 | 94 | 1465 | 222 | 4634 | 0 | 558 | 1538.5 | 0 | 0 | 8 | 101
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 371 | 06:00 | 360 | 13:00 | Payra | 407 | 06:00 | 402 | 18:00
Ashuganj | 397 | 1:00 | 374 | 14:00 | Rahanpur | 397 | 10:00 | 384 | 18:00
Bhulta | 389 | 04:00 | 364 | 12:00 | Rampal | 399 | 06:00 | 388 | 00:00
Bibiana | 382 | 06:00 | 376 | 12:00
BIPTC | 405 | 06:00 | 397 | 18:30
Bogura | 386 | 10:00 | 370 | 18:00
Gopalganj | 388 | 06:00 | 377 | 18:00
Kaliakoir | 363 | 04:00 | 352 | 12:00
Madunaghat | 390 | 21:00 | 383 | 10:00
Meghnaghat | 395 | 23:00 | 363 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 222 | 06:00 | 213 | 12:00 | Kaliakoir | 225 | 04:00 | 215 | 12:00
AKSML | 231 | 20:00 | 224 | 03:00 | Keranigonj | 218 | 05:00 | 210 | 11:00
Aminbazar | 221 | 02:00 | 212 | 15:00 | Khulna(S) | 229 | 05:00 | 218 | 18:00
Ashuganj | 222 | 00:00 | 212 | 09:00 | Madunaghat | 231 | 19:00 | 225 | 09:00
Ashuganj-400 | 222 | 00:00 | 212 | 09:00 | Madunaghat-400 | 231 | 18:00 | 226 | 04:00
Baghabari | 232 | 00:00 | 224 | 12:00 | Maniknagar | 212 | 05:00 | 207 | 11:00
Barapukuria | 223 | 01:00 | 204 | 18:00 | Meghnaghat | 221 | 06:00 | 215 | 10:00
Barapukuria-230 | 223 | 01:00 | 204 | 18:00 | Meghnaghat-400 | 216 | 05:00 | 211 | 11:00
Barishal | 231 | 06:00 | 224 | 18:30 | Mirsorai | 229 | 18:30 | 217 | 04:00
Bheramara | 234 | 01:00 | 222 | 18:00 | Rajshahi | 234 | 05:00 | 221 | 12:00
Bhulta | 222 | 04:00 | 205 | 14:00 | Rampal | 229 | 06:00 | 218 | 18:00
Bibiana | 224 | 01:00 | 220 | 16:00 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 238 | 04:00 | 223 | 12:00 | Rampura | 222 | 01:00 | 200 | 13:00
Bogura | 234 | 01:00 | 225 | 18:00 | Shikalbaha | 230 | 14:00 | 224 | 07:00
Bogura-400 | 235 | 10:00 | 225 | 18:00 | Shyampur | 216 | 05:00 | 210 | 11:00
Borhanuddin | 235 | 08:00 | 229 | 23:00 | Siddhirganj | 214 | 05:00 | 209 | 15:00
BSRM | 226 | 18:30 | 218 | 04:00 | Sirajgonj | 237 | 01:00 | 230 | 18:00
Cumilla(N) | 219 | 03:00 | 214 | 09:00 | Sreepur | 222 | 01:00 | 215 | 11:00
Faridpur | 228 | 06:00 | 220 | 00:00 | Tongi | 219 | 00:00 | 206 | 12:00
Fenchuganj | 227 | 06:00 | 222 | 16:00
Ghorashal | 225 | 01:00 | 220 | 00:00
Ghorashal-230 | 221 | 01:00 | 207 | 12:00
Gopalganj | 229 | 06:00 | 222 | 18:00
GPH | 229 | 18:30 | 222 | 04:00
Haripur | 214 | 06:00 | 209 | 11:00
Hasnabad | 217 | 05:00 | 209 | 12:00
Hathazari | 229 | 14:00 | 223 | 16:00
Ishurdi | 237 | 01:00 | 224 | 18:00
Jhenaidah | 232 | 05:00 | 215 | 18:00
Kachua | 228 | 14:00 | 215 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 01:00 | 121 | 12:00 | Lalmonirhat | 130 | 10:00 | 117 | 18:00
Agargaon | 130 | 05:00 | 122 | 12:00 | Madanganj | 128 | 03:00 | 126 | 00:00
Agrabad | 133 | 17:00 | 129 | 03:00 | Madaripur | 133 | 05:00 | 128 | 18:00
AKS | 130 | 13:00 | 127 | 09:00 | Madartek | 135 | 05:00 | 122 | 14:00
Aminbazar | 130 | 02:00 | 124 | 11:00 | Madunaghat | 134 | 14:00 | 131 | 05:00
Amnura | 136 | 00:00 | 126 | 13:00 | Magura | 135 | 07:00 | 123 | 18:00
Ashuganj | 136 | 04:00 | 131 | 16:00 | Mahasthangarh | 131 | 01:00 | 123 | 14:00
Bagerhat | 128 | 08:00 | 115 | 18:00 | Maijdee | 131 | 14:00 | 123 | 23:00
Bajitpur | 127 | 08:00 | 119 | 13:00 | Manikganj | 124 | 23:00 | 118 | 12:00
Bakulia | 135 | 21:00 | 129 | 05:00 | Maniknagar | 129 | 05:00 | 123 | 11:00
Banani | 138 | 01:00 | 122 | 14:00 | Matarbari | 121 | 14:00 | 107 | 01:00
Bangabhaban | 129 | 04:00 | 123 | 11:00 | Matuail | 124 | 04:00 | 121 | 11:00
Barapukuria | 137 | 01:00 | 122 | 18:00 | Metrorail_Motijheel | 129 | 05:00 | 123 | 11:00
Barguna | 134 | 07:00 | 130 | 00:00 | Metrorail_Uttara | 129 | 20:00 | 117 | 12:00
Barishal | 132 | 05:00 | 127 | 00:00 | Millgate | 129 | 21:00 | 118 | 12:00
Barishal-230 | 133 | 06:00 | 127 | 18:00 | Mirpur | 129 | 03:00 | 122 | 12:00
Baroaulia | 133 | 22:00 | 128 | 12:00 | Mirzapur | 127 | 04:00 | 122 | 14:00
Baroirhat | 130 | 14:00 | 124 | 23:00 | Mithapukur | 131 | 00:00 | 121 | 14:00
Bashundhara | 135 | 00:00 | 122 | 12:00 | MI_Cement | 124 | 06:00 | 121 | 00:00
BashundharaCement | 128 | 03:00 | 119 | 14:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 127 | 05:00 | 122 | 16:00 | Mogbazar | 137 | 06:00 | 125 | 11:00
Benapole | 134 | 04:00 | 116 | 18:00 | Mongla | 128 | 06:00 | 116 | 18:00
Bhaluka | 128 | 08:00 | 118 | 14:00 | Motijheel | 129 | 04:00 | 123 | 11:00
Bhandaria | 125 | 08:00 | 110 | 00:00 | Muktagacha | 130 | 10:00 | 120 | 14:00
Bhangura | 133 | 06:00 | 126 | 18:00 | Munshiganj | 123 | 20:00 | 120 | 00:00
Bheramara | 138 | 01:00 | 132 | 18:00 | Muradnagar | 125 | 14:00 | 120 | 03:00
Bheramara(GK) | 138 | 04:00 | 133 | 18:00 | Mymensingh | 130 | 10:00 | 111 | 18:00
Bhulta | 121 | 04:00 | 117 | 16:00 | Naogaon | 127 | 04:00 | 119 | 13:00
Bog-Sherpur | 132 | 01:00 | 126 | 13:00 | Narail | 137 | 06:00 | 122 | 18:00
Bogura | 132 | 00:00 | 125 | 14:00 | Narinda | 129 | 05:00 | 123 | 11:00
Bogura-230 | 134 | 01:00 | 127 | 13:00 | Narshingdi | 127 | 01:00 | 116 | 02:00
Brahmanbaria | 128 | 05:00 | 123 | 18:30 | Natore | 134 | 04:00 | 128 | 12:00
Cantonment | 129 | 04:00 | 122 | 12:00 | Nawabganj | 128 | 04:00 | 122 | 12:00
Chandina | 128 | 14:00 | 124 | 22:00 | Netrakona | 121 | 01:00 | 108 | 19:00
Chandpur | 137 | 14:00 | 129 | 09:00 | New | 130 | 21:00 | 118 | 12:00
Chandraghona | 134 | 13:00 | 131 | 04:00 | Niamatpur | 135 | 06:00 | 130 | 18:00
Chapai | 133 | 16:00 | 130 | 00:00 | Noapara | 133 | 06:00 | 123 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 124 | 06:00 | 120 | 11:00 | Pabna | 136 | 05:00 | 129 | 18:30
Chauddagram | 128 | 13:00 | 123 | 23:00 | Palashbari | 128 | 00:00 | 119 | 01:00
Chhatak | 127 | 07:00 | 119 | 18:00 | Panchagarh | 140 | 01:00 | 119 | 14:00
Chowmuhani | 130 | 12:00 | 123 | 23:00 | Patiya | 133 | 17:00 | 126 | 04:00
Chuadanga | 133 | 06:00 | 118 | 18:00 | Patuakhali | 134 | 07:00 | 130 | 00:00
Coxsbazar | 123 | 15:00 | 109 | 00:00 | Payra | 135 | 04:00 | 133 | 00:00
Cumilla(N) | 128 | 03:00 | 123 | 23:00 | PHP | 129 | 12:00 | 124 | 23:00
Cumilla(S) | 131 | 04:00 | 124 | 23:00 | Postogola | 129 | 04:00 | 123 | 11:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 136 | 07:00 | 122 | 12:00
Daudkandi | 122 | 14:00 | 116 | 11:00 | Purbasadipur | 134 | 01:00 | 116 | 14:00
DhakaUniversity | 138 | 01:00 | 122 | 14:00 | Rahanpur | 136 | 10:00 | 131 | 18:00
Dhamrai | 128 | 04:00 | 120 | 16:00 | Rahanpur-400 | 136 | 06:00 | 131 | 18:00
Dhanmondi | 136 | 00:00 | 123 | 11:00 | Rahim | 124 | 04:00 | 122 | 10:00
Dohazari | 129 | 17:00 | 123 | 00:00 | Rajbari | 133 | 05:00 | 127 | 18:00
Faridpur | 134 | 06:00 | 130 | 00:00 | Rajendrapur | 130 | 20:00 | 118 | 12:00
Fatullah | 132 | 08:00 | 126 | 11:00 | Rajshahi | 134 | 03:00 | 126 | 13:00
Fenchuganj | 134 | 04:00 | 130 | 23:00 | Rajshahi-230 | 134 | 05:00 | 127 | 12:00
Feni | 129 | 13:00 | 125 | 03:00 | Ramganj | 132 | 14:00 | 123 | 23:00
Ghatail | 128 | 05:00 | 117 | 22:00 | Rampur | 133 | 18:00 | 128 | 10:00
Ghorashal | 132 | 02:00 | 124 | 12:00 | Rampura | 137 | 01:00 | 121 | 13:00
Goalpara | 133 | 06:00 | 125 | 18:00 | Rangamati | 133 | 13:00 | 130 | 09:00
Gollamari | 133 | 06:00 | 125 | 18:00 | Rangpur | 133 | 01:00 | 120 | 14:00
Gopalganj | 132 | 06:00 | 126 | 18:00 | Ruppur | 138 | 04:00 | 132 | 18:00
Gopalganj-400 | 134 | 06:00 | 129 | 18:00 | Saidpur | 133 | 01:00 | 118 | 14:00
Gulshan | 136 | 00:00 | 121 | 09:00 | Satkhira | 130 | 05:00 | 119 | 18:00
Halishahar | 134 | 21:00 | 129 | 04:00 | Satmasjid | 129 | 06:00 | 121 | 13:00
Haripur | 125 | 06:00 | 122 | 11:00 | Savar | 130 | 20:00 | 122 | 12:00
HaripurSBU | 124 | 05:00 | 122 | 11:00 | SevenRings | 132 | 00:00 | 125 | 11:00
Hasnabad | 128 | 05:00 | 122 | 12:00 | ShahCement | 124 | 06:00 | 120 | 11:00
Hathazari | 135 | 14:00 | 131 | 05:00 | Shahjadpur | 136 | 02:00 | 131 | 12:00
Ishurdi | 139 | 01:00 | 133 | 13:00 | Shahjibazar | 130 | 07:00 | 124 | 18:30
Jaldhaka | 130 | 00:00 | 117 | 14:00 | Shahmirpur | 135 | 21:00 | 130 | 07:00
Jamalpur | 128 | 10:00 | 118 | 22:00 | Shariatpur | 133 | 06:00 | 126 | 00:00
Jashore | 135 | 04:00 | 119 | 18:00 | Sherpur | 127 | 10:00 | 114 | 14:00
Jhenaidah | 137 | 05:00 | 123 | 18:00 | Shikalbaha | 123 | 13:00 | 119 | 09:00
Jhenaidah-230 | 138 | 05:00 | 124 | 18:00 | Shikalbaha-230 | 135 | 13:00 | 130 | 06:00
Joydebpur | 134 | 20:00 | 122 | 14:00 | Shitalakhya | 128 | 05:00 | 121 | 00:00
Joypurhat | 126 | 01:00 | 119 | 13:00 | Sholosohor | 134 | 14:00 | 130 | 04:00
Juldah | 135 | 21:00 | 130 | 01:00 | Shyampur | 131 | 20:00 | 126 | 12:00
Kabirpur | 131 | 19:00 | 116 | 12:00 | Shyampur-230 | 131 | 08:00 | 126 | 11:00
Kachua | 135 | 14:00 | 127 | 23:00 | Siddhirganj | 125 | 06:00 | 121 | 11:00
Kaliakoir | 132 | 19:30 | 123 | 16:00 | Sirajganj | 130 | 00:00 | 125 | 11:00
Kallyanpur | 131 | 05:00 | 125 | 11:00 | Sonargaon | 123 | 05:00 | 120 | 11:00
Kalurghat | 134 | 14:00 | 131 | 04:00 | Sreemongol | 130 | 08:00 | 124 | 18:00
Kamrangirchar | 129 | 06:00 | 121 | 12:00 | Sreepur | 128 | 01:00 | 123 | 16:00
Kaptai | 133 | 5:00 | 126 | 12:00 | Srinagar | 129 | 07:00 | 122 | 16:00
Kasba | 124 | 13:00 | 119 | 22:00 | SSM | 138 | 18:30 | 132 | 00:00
Kazla | 128 | 06:00 | 123 | 13:00 | Sunamganj | 124 | 12:00 | 117 | 18:00
Keranigonj | 130 | 06:00 | 122 | 16:00 | Sylhet | 128 | 07:00 | 124 | 16:00
Khagrachori | 132 | 13:00 | 130 | 00:00 | Sylhet-132 | 128 | 06:00 | 125 | 16:00
Khulna | 132 | 08:00 | 123 | 18:00 | Tangail | 126 | 04:00 | 118 | 22:00
Khulna(S) | 134 | 06:00 | 125 | 18:00 | Taraganj | 132 | 00:00 | 119 | 14:00
Khulshi | 132 | 20:00 | 127 | 09:00 | Thakurgaon | 139 | 01:00 | 117 | 07:00
Kishoreganj | 127 | 08:00 | 116 | 20:00 | TK | 134 | 19:00 | 131 | 08:00
Kodda | 130 | 19:00 | 119 | 11:00 | Tongi | 132 | 20:00 | 122 | 12:00
KSRM | 134 | 19:00 | 129 | 03:00 | Ullahpara | 132 | 03:00 | 126 | 12:00
Kulaura | 132 | 06:00 | 129 | 16:00 | Ullon | 137 | 01:00 | 123 | 11:00
Kurigram | 131 | 01:00 | 114 | 07:00 | Uttara | 130 | 04:00 | 122 | 12:00
Kushtia | 136 | 06:00 | 129 | 12:00 | UttaraNew | 129 | 20:00 | 116 | 12:00
Laksam | 133 | 14:00 | 126 | 23:00 | Zigatola | 130 | 07:00 | 122 | 12:00
Lakshmipur | 130 | 14:00 | 122 | 23:00
Lalbag | 129 | 04:00 | 121 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division