## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 26-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-10-2025 | during | 26-10-2025 | during | 26-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 404 | 409 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 4 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 92 | 195 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 324 | 326 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 28.4 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 138 | 149.36 | 149.36 | 149.36 | 149.36 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 45 | 55 | 55 | 35 | 35.01 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20.8 | 20 | 24 | 24 | 24 | 24 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 25 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 145 | 300 | 300 | 64 | 95 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 70 | 149 | 149 | 149 | 149 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 108 | 162 | 162 | 108 | 108 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 22 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 142 | 160 | 160 | 108 | 108 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 1686.3 | 2335.4 | 5827.4 | 5795.4 | 4470.94 | 4560.95
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 150 | 180 | 150 | 150 | 150 | 150 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 218 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 60 | 50 | 70 | 40 | 70 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 64 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 16 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 100 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.43 | 0 | 3.45 | 0 | 3.45 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 16 | 50 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 35 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 17 | 88 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 86 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1102 | 1174 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 1 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2201.43 | 2973.5 | 3605.17 | 3610.72 | 3017.67 | 3067.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 300 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 395 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 28 | 35 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 41 | 41 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 100 | 147 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 41 | 130 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 35 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 163 | 163 | 110 | 110 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 58 | 174 | 200 | 200 | 180 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 68 | 78 | 160 | 160 | 94 | 94 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 99 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 57 | 89 | 115 | 115 | 90 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1366 | 1736 | 2284.05 | 2224.05 | 1976.05 | 1925.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-10-2025 | during | 26-10-2025 | during | 26-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 151 | 157 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 49 | 48 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 48 | 48 | 48 | 48 | 48 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.62 | 0 | 41.12 | 0 | 41.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 305.62 | 270 | 373.42 | 330 | 319.92 | 276.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 20 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 146 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 162 | 160 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 10 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 312 | 312 | 330 | 330 | 330 | 330 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1147 | 1145 | 1221 | 1221 | 1156 | 1156
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 894 | 893 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 398 | 364 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 82.51 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 594 | 570 | 0 | 0 | 1096 | 1096 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2006.51 | 1946 | 2403 | 2318 | 2738 | 2653
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 303 | 622 | 0 | 0 | 170 | 170 | machine problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 16 | 32 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1095 | 1120 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 9 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 170 | 170 | 307 | 307 | 170 | 170 | machine problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.57 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1898.57 | 2283 | 2147 | 2146 | 1953 | 1968
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 36.34 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 47 | 47 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 182 | 175 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 334 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 12 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 96 | 96 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 83 | 113 | 113 | 113 | 113 | Fuel shortage as BPDB payment not done in time
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.41 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 963.78 | 1448 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63.84 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1773.37 | 2319.2 | 3188.37 | 3021.87 | 3007.59 | 2841.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.3 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 168 | 0 | 165.68 | 0 | 165.68 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 258.3 | 228 | 449.68 | 248 | 429.68 | 228
System Total |  |  |  |  | 28823.2 | 28364.092 | 12643.1 | 15236.1 | 21499.09 | 20915.04 | 19068.85 | 18675.81
Forecast Scenario (26-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14700 |  | 0 |  | 14700
|  |  |  | 1:00 | 14250 |  | 0 |  | 14250
|  |  |  | 2:00 | 13750 |  | 0 |  | 13750
|  |  |  | 3:00 | 13350 |  | 0 |  | 13350
|  |  |  | 4:00 | 13000 |  | 0 |  | 13000
|  |  |  | 5:00 | 12640 |  | 0 |  | 12640
|  |  |  | 6:00 | 12370 |  | 0 |  | 12370
|  |  |  | 7:00 | 12590 |  | 0 |  | 12590
|  |  |  | 8:00 | 12540 |  | 0 |  | 12540
|  |  |  | 9:00 | 12650 |  | 0 |  | 12650
|  |  |  | 10:00 | 12900 |  | 0 |  | 12900
|  |  |  | 11:00 | 13500 |  | 0 |  | 13500
|  |  |  | 12:00 | 13850 |  | 0 |  | 13850
|  |  |  | 13:00 | 14150 |  | 0 |  | 14150
|  |  |  | 14:00 | 13940 |  | 0 |  | 13940
|  |  |  | 15:00 | 14050 |  | 0 |  | 14050
|  |  |  | 16:00 | 13850 |  | 0 |  | 13850
|  |  |  | 17:00 | 13600 |  | 0 |  | 13600
|  |  |  | 18:00 | 15480 |  | 0 |  | 15480
|  |  |  | 18:30 | 15500 |  | 0 |  | 15500
|  |  |  | 19:00 | 15510 |  | 0 |  | 15510
|  |  |  | 19:30 | 15450 |  | 0 |  | 15450
|  |  |  | 20:00 | 15380 |  | 0 |  | 15380
|  |  |  | 21:00 | 15200 |  | 0 |  | 15200
|  |  |  | 22:00 | 14900 |  | 0 |  | 14900
|  |  |  | 23:00 | 14630 |  | 0 |  | 14630
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 13850.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15510.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15510.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 332.78 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:06 hrs on 26-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 25-10-2025 | [28 empty] | Date: | 25-10-2025 | [28 empty] | Date: | 25-10-2025 | [28 empty] | Date: | 25-10-2025 | [28 empty] | Date: | 25-10-2025 | [14 empty] | Date: | 25-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [14 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 46.7 | 0 | 52 | 15 | 45 | 0 | 17 | 138 | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 36 | 0 | 0 | 100 | 15 | 22 | 0 | 0 | 86 | 0 | 19 | 150 | 0 | 65 | 0 | 0 | 100 | 88 | 0 | 220 | 0 | 29 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 0 | 51 | 0 | 160 | 350 | 352 | 0 | 42 | 0 | 34 | 47 | 103 | 94 | 0 | 19 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 312 | 0 | 67 | 150 | 10 | 0 | 83 | 30 | 0 | 17 | 161 | 17 | 49 | 48 | 158 | 0 | 0 | 6 | 6995.7 | 887 | 388 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1188 | 0 | 1456.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 551 | 1156 | 0 | 6823.56 | 13819.26 | 104.95
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 21.7 | 0 | 52 | 15 | 15 | 0 | 0 | 126 | 0 | 450 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 | 70 | 14 | 22 | 0 | 0 | 86 | 0 | 22 | 150 | 0 | 50 | 0 | 0 | 100 | 88 | 0 | 220 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1172 | 0 | 51 | 0 | 155 | 393 | 348 | 0 | 42 | 0 | 37 | 57 | 103 | 154 | 0 | 19 | 0 | 78 | 0 | 0 | 0 | 305 | 0 | 312 | 0 | 67 | 143 | 10 | 0 | 83 | 30 | 0 | 17 | 161 | 17 | 49 | 48 | 158 | 0 | 0 | 6 | 6847.7 | 887 | 377 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 0 | 1462.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 35 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 180 | 0 | 552 | 1185 | 0 | 6648.81 | 13496.51 | 104.94
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17.5 | 0 | 30 | 0 | 0 | 0 | 0 | 126 | 0 | 450 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 | 70 | 15 | 22 | 0 | 0 | 15 | 0 | 50 | 150 | 0 | 50 | 0 | 0 | 88 | 88 | 0 | 218 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1133 | 0 | 51 | 0 | 107 | 335 | 354 | 0 | 43 | 0 | 37 | 78 | 103 | 173 | 0 | 19 | 0 | 80 | 0 | 0 | 0 | 305 | 0 | 312 | 0 | 67 | 152 | 7 | 0 | 83 | 30 | 0 | 17 | 161 | 17 | 49 | 48 | 160 | 0 | 0 | 6 | 6660.5 | 887 | 372 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 595 | 0 | 1471.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 180 | 0 | 552 | 1214 | 0 | 6178.36 | 12838.86 | 104.93
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17.5 | 0 | 17 | 0 | 0 | 0 | 0 | 90 | 0 | 450 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 | 52 | 15 | 22 | 0 | 0 | 0 | 0 | 50 | 150 | 0 | 33 | 0 | 0 | 88 | 60 | 0 | 218 | 0 | 40 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 | 0 | 51 | 0 | 76 | 340 | 357 | 0 | 43 | 0 | 37 | 0 | 103 | 17 | 0 | 13 | 0 | 78 | 0 | 0 | 0 | 310 | 0 | 312 | 0 | 67 | 146 | 7 | 0 | 83 | 30 | 0 | 17 | 161 | 17 | 49 | 48 | 161 | 0 | 0 | 6 | 6296.5 | 887 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 1450.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 180 | 0 | 552 | 1214 | 0 | 6093.71 | 12390.21 | 104.92
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17.5 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 | 52 | 14 | 22 | 0 | 0 | 0 | 0 | 24 | 150 | 0 | 20 | 0 | 0 | 88 | 36 | 0 | 218 | 0 | 40 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 0 | 51 | 0 | 76 | 393 | 354 | 0 | 43 | 0 | 37 | 0 | 104 | 0 | 0 | 13 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 312 | 0 | 67 | 147 | 7 | 0 | 81 | 30 | 0 | 17 | 161 | 0 | 49 | 48 | 161 | 0 | 0 | 6 | 6188.5 | 888 | 390 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 601 | 0 | 1333.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 180 | 0 | 455 | 1216 | 0 | 5927.42 | 12115.92 | 104.91
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17.5 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 300 | 36 | 0 | 0 | 35 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 48 | 36 | 0 | 218 | 0 | 40 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 0 | 51 | 0 | 76 | 382 | 351 | 0 | 43 | 0 | 37 | 0 | 104 | 0 | 0 | 13 | 0 | 68 | 0 | 0 | 0 | 305 | 0 | 312 | 0 | 67 | 144 | 7 | 0 | 81 | 30 | 0 | 17 | 161 | 0 | 49 | 8 | 161 | 0 | 0 | 0 | 6044.5 | 888 | 397 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 594 | 0 | 1273.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 180 | 0 | 407 | 1118 | 0 | 5729.5 | 11774 | 104.9
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 300 | 36 | 0 | 0 | 17 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 48 | 12 | 0 | 218 | 0 | 42 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1145 | 0 | 51 | 0 | 76 | 393 | 356 | 0 | 43 | 0 | 37 | 0 | 104 | 0 | 0 | 13 | 0 | 68 | 0 | 0 | 0 | 310 | 0 | 312 | 0 | 67 | 146 | 7 | 0 | 81 | 30 | 0 | 17 | 161 | 0 | 49 | 8 | 161 | 0 | 0 | 0 | 5965 | 888 | 368 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 588 | 0 | 1273.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 180 | 0 | 345 | 1048 | 0 | 5529.45 | 11494.45 | 104.89
07:00 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 300 | 36 | 0 | 4 | 17 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 4 | 0 | 0 | 0 | 24 | 12 | 0.39 | 218 | 0 | 39 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1155 | 5 | 51 | 0 | 76 | 376 | 353 | 0 | 44 | 0 | 37 | 0 | 104 | 0 | 0 | 13 | 0 | 60 | 0 | 10 | 0 | 310 | 0 | 312 | 0 | 67 | 148 | 0 | 0 | 83 | 30 | 0 | 17 | 161 | 0 | 49 | 47 | 161 | 0 | 5.6 | 0 | 6010.99 | 888 | 400 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 590 | 0 | 1291.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.02 | 12 | 0 | 0 | 7.64 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.68 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.7 | 12 | 0.07 | 0 | 170 | 110 | 180 | 0 | 304 | 1042 | 0 | 5656.66 | 11667.65 | 104.88
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 331 | 97 | 0 | 12 | 17 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 150 | 1 | 0 | 0 | 0 | 24 | 12 | 1.3 | 219 | 0 | 7 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1152 | 11 | 51 | 0 | 16 | 364 | 353 | 0 | 44 | 0 | 38 | 0 | 101 | 0 | 0 | 13 | 0 | 62 | 0 | 29 | 0 | 320 | 0 | 312 | 0 | 67 | 155 | 7 | 0 | 83 | 30 | 0 | 17 | 161 | 0 | 49 | 47 | 160 | 1 | 19.05 | 5 | 6130.35 | 888 | 388 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32 | 560 | 0 | 1279.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.71 | 39 | 0 | 0 | 26.55 | 179 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 2.15 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 2.6 | 36 | 0.21 | 0 | 170 | 110 | 220 | 0 | 303 | 1070 | 0 | 5782.15 | 11912.5 | 104.87
09:00 | 0 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 17 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 280 | 39 | 0 | 20 | 35 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 24 | 12 | 2.25 | 219 | 0 | 4 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 15 | 51 | 0 | 8 | 320 | 350 | 0 | 43 | 0 | 28 | 0 | 101 | 0 | 0 | 13 | 0 | 60 | 0 | 46 | 0 | 300 | 0 | 312 | 0 | 67 | 148 | 7 | 0 | 80 | 30 | 0 | 17 | 161 | 0 | 49 | 48 | 159 | 2 | 30.37 | 6 | 5881.02 | 887 | 383 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54 | 565 | 0 | 1171.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.22 | 68 | 0 | 0 | 45.06 | 167 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 3.79 | 0 | 0 | 35 | 21 | 34 | 0 | 0 | 0 | 4.3 | 60 | 0.37 | 0 | 170 | 110 | 180 | 0 | 302 | 1094 | 0 | 5770.88 | 11651.9 | 104.86
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 35 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 325 | 94 | 0 | 26 | 35 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 9 | 0 | 0 | 0 | 12 | 0 | 3.2 | 221 | 0 | 5 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 18 | 51 | 0 | 8 | 389 | 346 | 0 | 42 | 0 | 21 | 0 | 100 | 0 | 0 | 20 | 0 | 68 | 0 | 59 | 0 | 320 | 0 | 312 | 0 | 67 | 150 | 7 | 0 | 81 | 20 | 0 | 17 | 161 | 0 | 49 | 48 | 153 | 1 | 39.45 | 0 | 6017.05 | 887 | 389 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70 | 490 | 0 | 1042.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.69 | 89 | 0 | 0 | 55.86 | 163 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 4.81 | 0 | 0 | 35 | 25 | 34 | 0 | 0 | 0 | 5.5 | 148 | 0.51 | 0 | 170 | 110 | 220 | 0 | 301 | 1048 | 0 | 5675.49 | 11692.54 | 104.86
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 0 | 34 | 0 | 0 | 0 | 35 | 62 | 0 | 450 | 0 | 0 | 0 | 0 | 325 | 93 | 0 | 30 | 35 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 2 | 0 | 0 | 0 | 36 | 12 | 3.49 | 221 | 0 | 2 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 20 | 51 | 1 | 40 | 393 | 345 | 0 | 42 | 0 | 27 | 1 | 100 | 1 | 0 | 20 | 0 | 70 | 0 | 63 | 0 | 325 | 0 | 312 | 0 | 67 | 159 | 7 | 0 | 81 | 30 | 0 | 17 | 162 | 10 | 49 | 48 | 153 | 2 | 45.68 | 0 | 6322.97 | 887 | 393 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 592 | 0 | 944.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.51 | 79 | 0 | 0 | 63.34 | 172 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 5.43 | 0 | 0 | 35 | 25 | 34 | 0 | 0 | 0 | 6.2 | 172 | 0.61 | 0 | 170 | 110 | 220 | 0 | 301 | 1030 | 0 | 5781.44 | 12104.41 | 104.85
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17.5 | 22 | 34 | 0 | 145 | 4 | 35 | 72 | 0 | 450 | 0 | 0 | 0 | 0 | 324 | 92 | 0 | 31 | 35 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1 | 0 | 0 | 0 | 36 | 17 | 3.43 | 221 | 0 | 2 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 19 | 51 | 41 | 100 | 393 | 340 | 0 | 41 | 0 | 28 | 57 | 100 | 58 | 8 | 14 | 0 | 68 | 0 | 67 | 0 | 315 | 0 | 312 | 0 | 67 | 156 | 8 | 0 | 80 | 30 | 0 | 17 | 162 | 17 | 49 | 49 | 151 | 2 | 37.62 | 0 | 6706.35 | 894 | 398 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82.51 | 594 | 0 | 963.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.34 | 108 | 0 | 0 | 63.84 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.41 | 0 | 0 | 35 | 15 | 34 | 0 | 0 | 0 | 6.3 | 168 | 0.57 | 0 | 170 | 110 | 220 | 0 | 303 | 1095 | 0 | 5936.75 | 12643.1 | 104.85
13:00 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17.5 | 46 | 34 | 15 | 145 | 38 | 35 | 72 | 0 | 450 | 0 | 0 | 0 | 0 | 322 | 90 | 0 | 0 | 52 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 36 | 32 | 2.98 | 221 | 0 | 3 | 650 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 18 | 51 | 85 | 140 | 395 | 335 | 0 | 41 | 0 | 33 | 68 | 99 | 84 | 9 | 7 | 0 | 76 | 0 | 56 | 0 | 320 | 0 | 312 | 0 | 67 | 156 | 8 | 0 | 80 | 30 | 0 | 17 | 162 | 17 | 49 | 49 | 151 | 1 | 31.28 | 0 | 6918.26 | 894 | 393 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 75.56 | 602 | 0 | 1124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.07 | 100 | 0 | 0 | 60.42 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.11 | 0 | 0 | 35 | 20 | 34 | 0 | 0 | 0 | 5.1 | 125 | 0.19 | 0 | 170 | 110 | 220 | 0 | 453 | 1123 | 0 | 6223.45 | 13141.71 | 104.84
14:00 | 0 | 37 | 24 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17.5 | 54 | 35 | 45 | 81 | 55 | 35 | 72 | 0 | 450 | 0 | 0 | 0 | 17 | 319 | 130 | 0 | 0 | 70 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 36 | 36 | 2.41 | 221 | 0 | 2 | 650 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 2 | 51 | 102 | 143 | 395 | 343 | 0 | 39 | 0 | 33 | 68 | 97 | 84 | 0 | 7 | 0 | 80 | 0 | 51 | 0 | 315 | 0 | 312 | 0 | 67 | 154 | 8 | 0 | 80 | 30 | 0 | 17 | 162 | 17 | 48 | 49 | 151 | 0 | 34.61 | 1 | 7019.02 | 894 | 385 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55 | 590 | 0 | 1176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.21 | 78 | 0 | 0 | 50.31 | 183 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 4.4 | 0 | 0 | 35 | 25 | 34 | 0 | 0 | 0 | 2 | 135 | 0.32 | 0 | 170 | 110 | 220 | 0 | 500 | 1120 | 0 | 6207.24 | 13226.26 | 104.84
15:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17.5 | 54 | 35 | 45 | 81 | 55 | 35 | 72 | 0 | 450 | 0 | 0 | 0 | 17 | 319 | 131 | 0 | 0 | 70 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 88 | 75 | 1.63 | 214 | 0 | 2 | 650 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 11 | 51 | 105 | 143 | 395 | 339 | 0 | 39 | 0 | 31 | 68 | 98 | 81 | 0 | 12 | 0 | 76 | 0 | 36 | 6 | 320 | 0 | 312 | 0 | 67 | 155 | 8 | 0 | 80 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 151 | 1 | 25.57 | 6 | 7218.2 | 893 | 394 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 37.54 | 595 | 0 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.14 | 62 | 0 | 0 | 35.44 | 186 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 3.18 | 0 | 0 | 44 | 9 | 50 | 0 | 0 | 0 | 3.2 | 102 | 0.26 | 0 | 170 | 110 | 220 | 0 | 501 | 1120 | 0 | 6198.76 | 13416.96 | 104.83
16:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 22 | 0 | 35 | 15 | 81 | 55 | 35 | 72 | 0 | 450 | 0 | 0 | 0 | 0 | 320 | 75 | 0 | 0 | 52 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 88 | 100 | 0.75 | 214 | 0 | 2 | 650 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 6 | 51 | 107 | 143 | 395 | 344 | 0 | 39 | 0 | 32 | 68 | 98 | 77 | 0 | 12 | 0 | 76 | 0 | 17 | 20 | 305 | 0 | 312 | 0 | 67 | 142 | 5 | 0 | 80 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 152 | 1 | 11.46 | 6 | 7032.71 | 893 | 385 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 590 | 0 | 1176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 16.62 | 32 | 0 | 0 | 17.48 | 175 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 1.56 | 0 | 0 | 95 | 7 | 106 | 0 | 0 | 0 | 1.6 | 49 | 0.13 | 0 | 170 | 110 | 220 | 0 | 500 | 1110 | 0 | 6109.39 | 13142.1 | 104.83
17:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 26 | 35 | 30 | 81 | 55 | 35 | 72 | 0 | 450 | 0 | 0 | 0 | 0 | 310 | 133 | 0 | 0 | 52 | 20 | 22 | 0 | 0 | 1 | 16 | 5 | 180 | 5 | 32 | 7 | 0 | 100 | 100 | 0.02 | 214 | 0 | 10 | 650 | 35 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1185 | 1 | 51 | 108 | 145 | 350 | 300 | 0 | 36 | 0 | 32 | 68 | 99 | 83 | 0 | 17 | 0 | 76 | 0 | 2 | 33 | 320 | 0 | 312 | 0 | 67 | 147 | 5 | 0 | 83 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 153 | 0 | 1.39 | 6 | 7175.41 | 893 | 380 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 591 | 0 | 1246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 52.2 | 1.66 | 4 | 0 | 0 | 1.74 | 169 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0.15 | 0 | 0 | 95 | 1 | 113 | 0 | 0 | 0 | 0.3 | 6 | 0.02 | 0 | 170 | 110 | 180 | 0 | 501 | 1000 | 9 | 5920.07 | 13095.48 | 104.82
18:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 8 | 35 | 60 | 128 | 145 | 55 | 35 | 108 | 0 | 450 | 0 | 0 | 0 | 17 | 328 | 195 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 90 | 16 | 50 | 180 | 0 | 64 | 32 | 29 | 100 | 88 | 0 | 214 | 0 | 14 | 650 | 160 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 1187 | 0 | 51 | 120 | 145 | 395 | 347 | 0 | 40 | 0 | 34 | 80 | 102 | 117 | 0 | 17 | 81 | 80 | 43 | 0 | 34 | 310 | 0 | 312 | 20 | 67 | 148 | 10 | 0 | 83 | 30 | 0 | 17 | 160 | 17 | 48 | 48 | 154 | 0 | 0 | 6 | 8297 | 894 | 377 | 0 | 33 | 10 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 0 | 1455 | 0 | 47 | 0 | 35 | 14 | 0 | 96 | 20 | 52.2 | 0 | 0 | 12 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 170 | 110 | 220 | 0 | 623 | 1030 | 9 | 6657.2 | 14954.2 | 104.82
19:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 28.4 | 35 | 70 | 138 | 145 | 55 | 45 | 108 | 0 | 450 | 0 | 0 | 0 | 17 | 326 | 195 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 86 | 16 | 100 | 180 | 1 | 64 | 60 | 35 | 100 | 88 | 0 | 218 | 0 | 16 | 650 | 160 | 0 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 1174 | 0 | 51 | 130 | 147 | 395 | 300 | 0 | 41 | 0 | 35 | 89 | 100 | 174 | 0 | 19 | 99 | 78 | 43 | 0 | 35 | 300 | 0 | 312 | 20 | 67 | 146 | 10 | 0 | 83 | 30 | 0 | 17 | 160 | 17 | 48 | 48 | 157 | 0 | 0 | 0 | 8459.9 | 893 | 364 | 0 | 41 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 0 | 1448 | 0 | 47 | 0 | 35 | 83 | 0 | 95 | 38 | 52.2 | 0 | 0 | 12 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 170 | 110 | 220 | 0 | 622 | 1120 | 9 | 6776.2 | 15236.1 | 104.81
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 51 | 35 | 70 | 106 | 145 | 55 | 55 | 108 | 0 | 450 | 0 | 0 | 0 | 17 | 326 | 195 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 82 | 16 | 105 | 180 | 0 | 64 | 60 | 35 | 100 | 88 | 0 | 218 | 0 | 18 | 650 | 53 | 0 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 1183 | 0 | 51 | 132 | 147 | 395 | 342 | 0 | 41 | 0 | 35 | 90 | 102 | 185 | 0 | 19 | 30 | 80 | 43 | 0 | 35 | 310 | 0 | 312 | 20 | 67 | 140 | 10 | 0 | 83 | 30 | 0 | 17 | 160 | 17 | 48 | 48 | 157 | 0 | 0 | 2 | 8359.5 | 893 | 386 | 0 | 34 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 0 | 1471 | 0 | 47 | 0 | 35 | 108 | 0 | 95 | 38 | 52.2 | 0 | 0 | 12 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 170 | 110 | 220 | 0 | 620 | 1090 | 9 | 6827.2 | 15186.7
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 51 | 35 | 70 | 106 | 145 | 55 | 55 | 108 | 0 | 450 | 0 | 0 | 0 | 17 | 326 | 196 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 84 | 16 | 105 | 180 | 0 | 64 | 60 | 35 | 100 | 88 | 0 | 218 | 0 | 25 | 650 | 53 | 0 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 1160 | 0 | 51 | 133 | 147 | 395 | 352 | 0 | 43 | 0 | 35 | 91 | 102 | 178 | 0 | 19 | 29 | 76 | 43 | 0 | 35 | 305 | 0 | 312 | 20 | 67 | 141 | 10 | 0 | 83 | 30 | 0 | 18 | 160 | 17 | 48 | 48 | 157 | 0 | 0 | 3 | 8348.5 | 893 | 358 | 0 | 34 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 0 | 1457 | 0 | 47 | 0 | 35 | 111 | 0 | 95 | 38 | 52.2 | 0 | 0 | 12 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 170 | 110 | 220 | 0 | 622 | 1093 | 9 | 6793.2 | 15141.7 | 104.8
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 52.5 | 35 | 70 | 106 | 145 | 55 | 35 | 108 | 0 | 450 | 0 | 0 | 0 | 17 | 270 | 135 | 0 | 0 | 142 | 20 | 22 | 0 | 0 | 91 | 16 | 105 | 180 | 0 | 64 | 60 | 35 | 100 | 100 | 0 | 220 | 0 | 31 | 650 | 17 | 0 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 51 | 133 | 147 | 350 | 300 | 0 | 42 | 0 | 36 | 90 | 102 | 180 | 0 | 19 | 32 | 80 | 43 | 0 | 29 | 315 | 0 | 312 | 20 | 67 | 152 | 10 | 0 | 83 | 30 | 0 | 17 | 160 | 17 | 48 | 48 | 157 | 0 | 0 | 6 | 8028 | 901 | 403 | 0 | 34 | 33 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 591 | 0 | 1455 | 0 | 47 | 0 | 35 | 113 | 0 | 95 | 38 | 52.2 | 0 | 0 | 12 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 170 | 110 | 180 | 0 | 623 | 1098 | 9 | 6855.2 | 14883.2 | 104.79
22:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 51.7 | 35 | 70 | 90 | 147 | 15 | 35 | 108 | 0 | 450 | 0 | 0 | 0 | 17 | 270 | 135 | 0 | 0 | 142 | 21 | 22 | 0 | 82 | 45 | 16 | 82 | 180 | 0 | 65 | 60 | 17 | 100 | 100 | 0 | 220 | 0 | 31 | 650 | 17 | 0 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 51 | 133 | 147 | 395 | 300 | 0 | 43 | 0 | 36 | 87 | 102 | 186 | 0 | 19 | 31 | 82 | 43 | 0 | 35 | 320 | 0 | 312 | 20 | 67 | 155 | 10 | 0 | 83 | 30 | 0 | 18 | 160 | 17 | 48 | 48 | 158 | 0 | 0 | 6 | 8058.2 | 901 | 396 | 0 | 34 | 36 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 605 | 0 | 1464 | 0 | 47 | 0 | 35 | 113 | 0 | 95 | 38 | 8 | 0 | 0 | 12 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 170 | 110 | 220 | 0 | 566 | 1102 | 9 | 6821 | 14879.2 | 104.79
23:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 47 | 35 | 38 | 90 | 145 | 15 | 35 | 54 | 0 | 450 | 0 | 0 | 0 | 17 | 330 | 196 | 0 | 0 | 35 | 21 | 22 | 0 | 71 | 46 | 16 | 76 | 180 | 0 | 65 | 60 | 17 | 100 | 100 | 0 | 219 | 0 | 34 | 620 | 17 | 0 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 51 | 133 | 147 | 395 | 352 | 0 | 43 | 0 | 36 | 57 | 103 | 177 | 0 | 19 | 31 | 84 | 43 | 0 | 35 | 310 | 0 | 312 | 20 | 67 | 146 | 9 | 0 | 81 | 30 | 0 | 18 | 161 | 17 | 48 | 48 | 158 | 0 | 0 | 6 | 7945.5 | 904 | 387 | 0 | 34 | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 605 | 0 | 1470 | 0 | 47 | 0 | 35 | 113 | 0 | 95 | 38 | 8 | 0 | 0 | 12 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 170 | 110 | 220 | 0 | 550 | 1098 | 9 | 6755 | 14700.5 | 104.78
Total KWH | 0 | 1062720 | 323040 | 0 | 0 | 0 | 0 | 0 | 9363600 | 0 | 0 | 518400 | 496440 | 911952 | 829440 | 1590513 | 547662 | 529249 | 1565280 | 0 | 10163500 | 0 | 0 | 0 | 137174 | 7256921 | 2483000 | 0 | 104024 | 1616400 | 423600 | 366840 | 0 | 150000 | 712582 | 115418 | 727680 | 3900000 | 30720 | 620721 | 357312 | 202759 | 1680960 | 1395840 | 20520 | 5261716 | 0 | 489120 | 15570909.09 | 470036 | 0 | 0 | 171651.6 | 0 | 30610 | 0 | 0 | 0 | 27692724 | 125820 | 1241152 | 1472000 | 2576000 | 9150000 | 8533500 | 0 | 1001280 | 0 | 818856 | 1116480 | 2404696 | 2092800 | 21000 | 370090 | 291840 | 1787520 | 287328 | 425918 | 272464 | 7607500 | 0 | 7850000 | 130000 | 1566360 | 3586745 | 205872 | 0 | 1946880 | 706176 | 0 | 419000 | 3357410 | 306000 | 1159200 | 1077600 | 3674880 | 11600 | 280780 | 95760 | 167861540.69 | 21598545 | 9483264 | 0 | 207360 | 205568 | 912000 | 0 | 0 | 0 | 0 | 0 | 524160 | 14712732 | 0 | 31159125 | 0 | 314258 | 0 | 246912 | 668640 | 0 | 593424 | 213152 | 306605 | 353114 | 679280 | 79976 | 0 | 427504 | 4305182 | 0 | 0 | 0 | 0 | 0 | 8949090 | 0 | 35820 | 0 | 0 | 1344184 | 171283 | 1474080 | 0 | 0 | 0 | 38078.16 | 997920 | 3343 | 192000 | 4123000 | 2639000 | 5157610 | 0 | 11249784 | 27208727.27 | 64800 | 150639520.43 | 318501061.12

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 25-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12643.1 | MW | 12:00 Hr. | Energy Generated |  |  | 318.5011 |  | MKWHr.
| Day Peak Demand |  |  | 12643.1 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.411 |  | MKWHr.
| Evening Peak Generation |  |  | 15236.1 | MW | 19:00 Hr. | Energy Demand |  |  | 318.9121 |  | MKWHr.
| Evening Peak Demand |  |  | 15331.1 | MW | 19:00 Hr. | Maximum Temperature |  |  | 34.1 |  | °C
| Minimum Generation of the Day |  |  | 11494.45 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 945.64 |  | MMCFD
| Maximum Generation of the Day |  |  | 15236.1 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.3922 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.2075 | 0 | 10.1283 | 0 | 0 | 0.10402 | 0 | 0 | 40.4398 | Gas | 122.3077 | Gas | 456395373.71
| Chattogram Zone |  |  | 4.4197 | 43.2636 | 6.455 | 0 | 5.2617 | 0.14634 | 0 | 0.03072 | 59.5771 | Coal | 100.5579 | Coal | 634560497.0327
| Cumilla Zone |  |  | 26.0956 | 0 | 5.5539 | 0 | 0 | 0.42592 | 1.7875 | 0 | 33.8629 | HFO | 30.6867 | HFO | 543868552.804
| Mymensingh Zone |  |  | 3.6749 | 0 | 2.6386 | 0 | 0 | 0.29238 | 0 | 0 | 6.6058 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.3759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3759 | Hydro | 5.2617 | Hydro | 526171.6
| Khulna Zone |  |  | 9.4833 | 14.7127 | 0.41293 | 0 | 0 | 0.52416 | 22.5105 | 0 | 47.6436 | Solar | 4.1992 | Solar | 66474746.0956
| Barishal Zone |  |  | 7.7966 | 42.5815 | 0.2568 | 0 | 0 | 0.003343 | 0 | 0 | 50.6383 | Import | 55.4572 | Import | 333642243.75
| Rajshahi Zone |  |  | 13.2543 | 0 | 2.423 | 0 | 0 | 1.4957 | 31.1591 | 0 | 48.3321 | Wind | 0.03072 | Wind | 451891.2
| Rangpur Zone |  |  | 0 | 0 | 2.8183 | 0 | 0 | 1.2073 | 0 | 0 | 4.0255
| Total |  |  | 122.3077 | 100.5579 | 30.6867 | 0 | 5.2617 | 4.1992 | 55.4572 | 0.03072 | 318.5011
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 456395373.71 |  | Hydro | 526171.6
|  |  |  | Coal | 634560497.0327 |  | Solar | 66474746.0956
|  |  |  | HFO | 543868552.804 |  | Import | 333642243.75
|  |  |  | HSD | 0 |  | Wind | 451891.2
[5 empty] | Total: | 203,59,19,476 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5985 | Peak Hr Flow | 893.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48694145.52 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.1591 | Peak Hr Flow | 1448.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1985 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.7875 | Peak Hr Flow | 78.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2570 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.5452 | Peak Hr Flow | 2419.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 9 |  | 5349
|  |  |  | Chattogram |  | 0 |  | 1595
|  |  |  | Cumilla |  | 0 |  | 1454
|  |  |  | Mymensingh |  | 49 |  | 1137
|  |  |  | Sylhet |  | 0 |  | 635
|  |  |  | Khulna |  | 33 |  | 1682
|  |  |  | Barishal |  | 0 |  | 454
|  |  |  | Rajshahi |  | 0 |  | 1405
|  |  |  | Rangpur |  | 0 |  | 922
|  |  |  | Total |  | 91 |  | 14633
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:06 | 15:11 | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to Yearly Maintanance Works
| 08:06 | 15:11 | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Yearly Maintanance Works
| 08:06 | 08:14 | Gollamari 132/33kV S/S Tr-2 LT Scheduled S/D Due to 33 kv bus-3 shutdown taken by wzpdcl | [7 empty] | 16.0MW load
interrup.
| 08:30 |  | BSRM-Mirsharai 230 kV Ckt-1 Scheduled S/D from Mirsorai 230/33kV end Due to Annual
Maintenance
| 08:41 | 16:05 | Barishal 230/132kV S/S 230kV BUS Scheduled S/D Due to Maintenance work
| 08:58 | 16:54 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Scheduled S/D Due to Annual
Maintenance
| 08:59 | 16:52 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Scheduled S/D Due to Annual
Maintenance
| 09:02 | 17:08 | Barapukuria 230/132/33kV S/S 132 KV Bus A Scheduled S/D Due to Annual Maintenance
| 09:15 | 12:55 | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to 413 GCB GAS leakage work
| 09:15 | 12:45 | Feni 132/33kV S/S T-2(415T) HT Scheduled S/D Due to 413 GCB GAS leakage work
| 09:16 | 15:49 | Muktagacha 132/33kV S/S RPCL-2 Scheduled S/D Due to Dead line checking
| 09:20 | 14:36 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to Auxiliary Transformer | [7 empty] | 20.0MW load
|  |  | Installation. | [7 empty] | interrup.
| 09:22 | 14:34 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to Auxiliary Transformer | [7 empty] | 20.0MW load
|  |  | Installation. | [7 empty] | interrup.
|  | 09:24 | Feni 132/33kV S/S T-1(405T) LT is restored.
|  | 09:24 | Feni 132/33kV S/S T-1(405T) HT is restored.
| 09:35 | 11:22 | Meghnaghat-Shyampur 230kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Shyampur 230 kV ckt-2 shutdown for nut bolt tightness.
| 09:41 | 14:08 | Bajitpur 132/33kV S/S Tr-1(404T) LT Scheduled S/D Due to Hot spot remove
| 09:42 | 14:07 | Bajitpur 132/33kV S/S Tr-1(404T) HT Scheduled S/D Due to Hot spot remove
| 09:48 |  | Sathia- Baghabari 132 KV ckt S/D due to OPGW stringing.
| 09:55 | 12:59 | Bogura-Bogura (New)) 132 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end Due to Red-hot
Maintenance and from Bogura 132/33kV end Due to Shutdown taken by Bogura 230/132 KV sub
statiuon.
| 09:57 | 12:44 | Bogura 230/132kV S/S 132KV Main 1 Scheduled S/D Due to Red Hot Maintenance
|  | 10:30 | Fenchuganj-Sreemangal 132kV Ckt-1 is restored.
| 11:28 | 12:16 | Meghnaghat-Shyampur 230kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to 230
kV Shyampur ckt- 1 shutdown for DS nut bolt tightness.
| 13:38 |  | Siddhirganj 2*120 MW GT-1 was synchronized.
| 13:47 |  | Sathia- Baghabari 132 KV ckt (Up to tower no. 268 including Bera 70 MW PS From Baghabari
end) charged from Sathia. 268 No. tower loop jumper is kept open.
| 14:44 | 14:47 | Gollamari 132/33kV S/S Tr-2 LT Scheduled S/D Due to 33kv bus section-3 shutdown | [7 empty] | 16.0MW load
|  |  | restoration | [7 empty] | interrup.
|  | 14:49 | Chauddagram-Cumilla(S) 132 kV Ckt-1 is restored.
| 15:25 | 16:05 | Bogura-Natore 132 kV Ckt-1 Forced S/D from Natore 132/33kV end.
| 15:25 | 16:05 | Bogura-Natore 132 kV Ckt-2 Forced S/D from Natore 132/33kV end.
| 15:28 | 17:13 | Ishwardi-Natore 132kV Ckt-1 Scheduled S/D from Ishurdi 132/33kV end Due to DS-667S "R''
phase red hot maintenance work and from Natore 132/33kVend.
|  | 16:33 | Patuakhali 132/33kV S/S 405T (T-1) HT is restored.
|  | 16:35 | Patuakhali 132/33kV S/S 405T (T-1) LT is restored.
|  | 17:17 | Madaripur 132/33kV S/S T1-405T HT is restored.
|  | 17:18 | Madaripur 132/33kV S/S T1-405T LT is restored.
|  | 17:25 | Rampur 230/132/33 S/S ATR-01 (706T) HT is restored.
|  | 17:25 | Rampur 230/132/33 S/S ATR-01 (706T) LT is restored.
|  | 17:51 | Madunaghat-Meghnaghat 400kV Ckt-1 is restored.
|  | 18:47 | Gopalganj 400/132kV S/S 400kV Rooppur is restored.
| 19:00 |  | Evening peak Generation is 15235 MW
| 21:47 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- GT
| 21:47 |  | Unique Meghnaghat Power Limited (UMPL) GT Synchronized with remarks:- GT Sync as per
Demand
| 23:40 |  | Unique Meghnaghat Power Limited (UMPL) ST Synchronized with remarks:- ST Sync as per NLDC
Demand
| 23:40 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
|  | 23:54 | Meghnaghat 400/230kV S/S 400 kV Bus -02 is restored.
| 06:00 |  | Minimum Generation: 12167 MW.
| 07:04 |  | Patuakhali 132/33kV S/S 405T (T-1) HT Scheduled S/D Due to Annual Maintenance-25
| 07:04 |  | Patuakhali 132/33kV S/S 405T (T-1) LT Scheduled S/D Due to Annual Maintenance-25
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 25-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 409 | 9363600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10163500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 547662 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 195 | 2483000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 7256921 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 28.4 | 518400 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 138 | 829440 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 45 | 529249 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 137174 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 423600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 366840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 323040 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 1590513 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 70 | 911952 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1062720 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1565280 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 104024 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 496440 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 150000 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1616400 | -
Dhaka Area Total |  |  |  |  | 6655.861 | 2335.4 | 40439755
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 180 | 3900000 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 171651.6 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125820 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 218 | 5261716 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 30610 | Under Maintenance
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 60 | 357312 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 64 | 620721 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1680960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 16 | 489120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 100 | 727680 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 115418 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 35 | 202759 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 1395840 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 86 | 712582 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 160 | 470036 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1174 | 27692724 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 1 | 30720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15570909.09 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2973.5 | 59577098.69
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 300 | 8533500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 395 | 9150000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 818856 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 41 | 1001280 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 147 | 2576000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1241152 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 130 | 1472000 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 272464 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2404696 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 174 | 2092800 | -
| Import (Tripura) |  | Import | 0 | 160 | 78 | 1787520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 287328 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 370090 | Schedule Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 99 | 291840 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 21000 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 1116480 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 425918 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1736 | 33862924
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 157 | 3674880 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 1077600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 48 | 1159200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 280780 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 95760 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 306000 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 270 | 6605820
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 20 | 130000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1566360 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 146 | 3586745 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 706176 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1946880 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 3357410 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 419000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 10 | 205872 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7607500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 312 | 7850000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1145 | 27375943
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 893 | 21598545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 41 | 207360 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 40 | 205568 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 364 | 9483264 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 524160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 570 | 14712732 | Unit 2 will be under shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 1946 | 47643629
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 622 | 11249784 | machine problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 192000 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2639000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 27208727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5157610 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 9 | 64800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 170 | 4123000 | machine problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3343 | -
Barishal Area Total |  |  |  |  | 2858 | 2283 | 50638264.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 353114 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 314258 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 213152 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 175 | 4305182 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 334 | 8949090 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 12 | 79976 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 306605 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 593424 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 83 | 668640 | Fuel shortage as BPDB payment not done in time
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 246912 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 35820 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1448 | 31159125 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 427504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 679280 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2319.2 | 48332082
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1474080 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38078.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1344184 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 171283 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 997920 | -
Rangpur Area Total |  |  |  |  | 950 | 228 | 4025545.16
Eastern Grid Total |  |  |  |  | 17383.852 | 8459.9 | 167861540.69
Western Grid Total |  |  |  |  | 10980.24 | 6776.2 | 150639520.43
National Grid Total |  |  |  |  | 28364.092 | 15236.1 | 318501061.12
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 25-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10111.46 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4430.3 | MW
i) Dhaka area |  |  | 5339.5 |  | MW | i) Khulna area |  |  |  | 1648.6 | MW
ii) Chattogram area |  |  | 1594.9 |  | MW | ii) Barishal area |  |  |  | 454.5 | MW
iii) Cumilla area |  |  | 1454.06 |  | MW | iii) Rajshahi area |  |  |  | 1405.2 | MW
iv) Mymensingh area |  |  | 1088 |  | MW | iv) Rangpur area |  |  |  | 922 | MW
v) Sylhet area |  |  | 635 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14541.76 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 87 | 18:30 | 133 | Niamatpur | 86 | 18:30
2 | AKSML | 161 | 07:00 | 68 | Ishurdi | 73 | 19:00 | 134 | Noapara | 45 | 20:00
3 | Aftabnagar | 38 | 00:00 | 69 | Jaldhaka | 77 | 18:30 | 135 | PHP | 7 | 04:00
4 | Agargaon | 127 | 14:00 | 70 | Jamalpur | 109 | 09:00 | 136 | Pabna | 98 | 18:30
5 | Agrabad | 88 | 18:30 | 71 | Jashore | 136 | 19:30 | 137 | Palashbari | 114 | 18:00
6 | Amnura | 34 | 13:00 | 72 | Jhenaidah | 130 | 18:30 | 138 | Panchagarh | 57 | 18:00
7 | Ashuganj | 89 | 00:00 | 73 | Joydebpur | 144 | 19:00 | 139 | Patiya | 11 | 18:30
8 | BSRM | 207 | 17:00 | 74 | Joypurhat | 57 | 20:00 | 140 | Patuakhali | 72 | 21:00
9 | Bagerhat | 80 | 18:00 | 75 | Juldah | 18.5 | 15:00 | 141 | Payra | 34 | 22:00
10 | Bajitpur | 70 | 01:00 | 76 | KSRM | 20 | 07:00 | 142 | Postogola | 67 | 13:00
11 | Bakulia | 89 | 19:30 | 77 | Kabirpur | 249 | 18:00 | 143 | Purbachal | 21 | 18:00
12 | Banani | 42.8 | 13:00 | 78 | Kachua | 94 | 19:30 | 144 | Purbasadipur | 119 | 19:00
13 | Bangabhaban | 11 | 11:00 | 79 | Kallyanpur | 108 | 18:30 | 145 | Rahanpur | 34 | 21:00
14 | Barapukuria | 61 | 19:00 | 80 | Kalurghat | 50 | 15:00 | 146 | Rahim | 44 | 15:00
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 78 | 16:00 | 147 | Rajbari | 76 | 18:00
16 | Barishal | 117 | 18:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 130 | 18:00
17 | Barishal-230 | 98 | 22:00 | 83 | Kasba | 37 | 22:00 | 149 | Rajshahi | 102 | 18:00
18 | Baroaulia | 65 | 12:00 | 84 | Kazla | 99 | 19:00 | 150 | Rajshahi-230 | 89 | 13:00
19 | Baroirhat | 62 | 20:00 | 85 | Keranigonj | 97 | 13:00 | 151 | Ramganj | 124 | 18:00
20 | Bashundhara | 196 | 14:00 | 86 | Khagrachori | 34 | 18:00 | 152 | Rampur | 44 | 19:00
21 | BashundharaCement | 15 | 21:00 | 87 | Khulna | 77 | 13:00 | 153 | Rangamati | 18 | 18:00
22 | Beanibazar | 76 | 18:00 | 88 | Khulshi | 203 | 18:00 | 154 | Rangpur | 145 | 18:00
23 | Benapole | 59 | 13:00 | 89 | Kishoreganj | 118 | 00:00 | 155 | Ruppur | 6 | 13:00
24 | Bhaluka | 154 | 18:30 | 90 | Kodda | 298 | 18:00 | 156 | SSM | 0 | 00:00
25 | Bhandaria | 54 | 22:00 | 91 | Kulaura | 53 | 19:30 | 157 | Saidpur | 100 | 18:30
26 | Bhangura | 36 | 18:00 | 92 | Kurigram | 60 | 19:00 | 158 | Satkhira | 124 | 20:00
27 | Bheramara(GK) | 64 | 18:00 | 93 | Kushtia | 148 | 18:30 | 159 | Satmasjid | 104 | 18:00
28 | Bhulta | 214 | 23:00 | 94 | Laksam | 34 | 23:00 | 160 | Savar | 224 | 18:00
29 | Bog-Sherpur | 60 | 18:00 | 95 | Lakshmipur | 33 | 19:30 | 161 | SevenRings | 14.45 | 02:00
30 | Bogura | 157 | 19:30 | 96 | Lalbag | 60 | 13:00 | 162 | ShahCement | 29 | 02:00
31 | Borhanuddin | 94 | 18:30 | 97 | Lalmonirhat | 57 | 18:00 | 163 | Shahjadpur | 85 | 19:00
32 | Brahmanbaria | 131 | 20:00 | 98 | MI_Cement | 8.8 | 03:00 | 164 | Shahjibazar | 123 | 22:00
33 | Cantonment | 164 | 19:00 | 99 | Madanganj | 42 | 12:00 | 165 | Shahmirpur | 54 | 17:00
34 | Chandina | 18.35 | 14:00 | 100 | Madaripur | 108 | 18:30 | 166 | Shariatpur | 90 | 22:00
35 | Chandpur | 82 | 18:00 | 101 | Madartek | 93 | 00:00 | 167 | Sherpur | 118 | 22:00
36 | Chandraghona | 37 | 18:00 | 102 | Madunaghat | 59 | 18:00 | 168 | Shikalbaha | 40.5 | 13:00
37 | Chapai | 67 | 21:00 | 103 | Magura | 65 | 18:30 | 169 | Shitalakhya | 84.6 | 12:00
38 | Charsaidpur | 25 | 19:30 | 104 | Mahasthangarh | 70 | 18:00 | 170 | Sholosohor | 48 | 16:00
39 | Chauddagram | 72 | 21:00 | 105 | Maijdee | 34 | 00:00 | 171 | Shyampur | 98 | 12:00
40 | Chhatak | 38 | 00:00 | 106 | Manikganj | 124 | 18:30 | 172 | Siddhirganj | 126 | 18:00
41 | Chowmuhani | 178 | 18:00 | 107 | Maniknagar | 62 | 18:00 | 173 | Sirajganj | 105 | 19:00
42 | Chuadanga | 105 | 18:30 | 108 | Matarbari | 55 | 18:00 | 174 | Sonargaon | 132 | 18:00
43 | Coxsbazar | 150 | 18:00 | 109 | Matuail | 72 | 15:00 | 175 | Sreemongol | 86 | 19:30
44 | Cumilla(N) | 145 | 18:00 | 110 | Metrorail_Motijheel | 16 | 13:00 | 176 | Sreepur | 110 | 18:00
45 | Cumilla(S) | 158 | 18:00 | 111 | Metrorail_Uttara | 19 | 18:00 | 177 | Srinagar | 46.8 | 22:00
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 131 | 16:00 | 178 | Sunamganj | 60 | 00:00
47 | Daudkandi | 144 | 21:00 | 113 | Mirpur | 129 | 21:00 | 179 | Sylhet | 52 | 01:00
48 | DhakaUniversity | 76 | 12:00 | 114 | Mirsorai | 13 | 19:00 | 180 | Sylhet-132 | 128 | 18:00
49 | Dhamrai | 130 | 18:30 | 115 | Mirzapur | 49 | 13:00 | 181 | TK | 24 | 18:30
50 | Dhanmondi | 132 | 13:00 | 116 | Mithapukur | 58 | 18:00 | 182 | Tangail | 174 | 18:30
51 | Dohazari | 109 | 22:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 22 | 18:00
52 | Faridpur | 157 | 19:00 | 118 | Mogbazar | 89.8 | 16:00 | 184 | Thakurgaon | 95 | 19:00
53 | Fatullah | 115 | 11:00 | 119 | Mongla | 36 | 18:00 | 185 | Tongi | 120 | 13:00
54 | Fenchuganj | 45 | 19:00 | 120 | Motijheel | 49 | 13:00 | 186 | Ullahpara | 36 | 18:00
55 | Feni | 133 | 18:00 | 121 | Muktagacha | 38 | 18:00 | 187 | Ullon | 67 | 22:00
56 | GPH | 80 | 13:00 | 122 | Munshiganj | 108 | 23:00 | 188 | Uttara | 89 | 18:00
57 | Ghatail | 82 | 18:00 | 123 | Muradnagar | 43 | 19:30 | 189 | UttaraNew | 41 | 23:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 202 | 19:00 | 190 | Zigatola | 73 | 15:00
59 | Ghorashal-230 | 102 | 16:00 | 125 | Naogaon | 125 | 18:30
60 | Goalpara | 42 | 18:00 | 126 | Narail | 57 | 18:30
61 | Gollamari | 92 | 00:00 | 127 | Narinda | 64 | 13:00
62 | Gopalganj | 103.2 | 18:00 | 128 | Narshingdi | 171 | 20:00
63 | Gulshan | 110 | 13:00 | 129 | Natore | 145 | 20:00
64 | Halishahar | 76 | 11:00 | 130 | Nawabganj | 55 | 21:00
65 | HaripurSBU | 133 | 23:00 | 131 | Netrakona | 126 | 20:00
66 | Hasnabad | 91 | 18:30 | 132 | New | 56 | 10:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 25-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13819.26 | 0 |  | 13819.26
1:00 | 13496.51 | 0 |  | 13496.51
2:00 | 12838.86 | 0 |  | 12838.86
3:00 | 12390.21 | 0 |  | 12390.21
4:00 | 12115.92 | 0 |  | 12115.92
5:00 | 11774 | 0 |  | 11774
6:00 | 11494.45 | 0 |  | 11494.45
7:00 | 11667.65 | 0 |  | 11667.65
8:00 | 11912.5 | 0 |  | 11912.5
9:00 | 11651.9 | 0 |  | 11651.9
10:00 | 11692.54 | 0 |  | 11692.54
11:00 | 12104.41 | 0 |  | 12104.41
12:00 | 12643.1 | 0 |  | 12643.1
13:00 | 13141.71 | 0 |  | 13141.71
14:00 | 13226.26 | 0 |  | 13226.26
15:00 | 13416.96 | 0 |  | 13416.96
16:00 | 13142.1 | 0 |  | 13142.1
17:00 | 13095.48 | 0 |  | 13095.48
18:00 | 14954.2 | 73 |  | 15030.2
19:00 | 15236.1 | 91 |  | 15331.1
19:30 | 15186.7 | 71 |  | 15260.7
20:00 | 15141.7 | 66 |  | 15210.7
21:00 | 14883.2 | 55 |  | 14940.2
22:00 | 14879.2 | 50 |  | 14931.45
23:00 | 14700.5 | 76 |  | 14779.92
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 25-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6995.7 | 6823.56 | 13819.26 | DAILY GENERATION CURVE
00:30 | 6921.7 | 6736.185 | 13657.885
01:00 | 6847.7 | 6648.81 | 13496.51 | 25-10-2025
01:30 | 6754.1 | 6413.585 | 13167.685
02:00 | 6660.5 | 6178.36 | 12838.86
02:30 | 6478.5 | 6136.035 | 12614.535
03:00 | 6296.5 | 6093.71 | 12390.21
03:30 | 6242.5 | 6010.565 | 12253.065
04:00 | 6188.5 | 5927.42 | 12115.92
04:30 | 6116.5 | 5828.46 | 11944.96
05:00 | 6044.5 | 5729.5 | 11774
05:30 | 6004.75 | 5629.475 | 11634.225
06:00 | 5965 | 5529.45 | 11494.45
06:30 | 5987.995 | 5593.055 | 11581.05
07:00 | 6010.99 | 5656.66 | 11667.65
07:30 | 6070.67 | 5719.405 | 11790.075
08:00 | 6130.35 | 5782.15 | 11912.5
08:30 | 6005.685 | 5776.515 | 11782.2
09:00 | 5881.02 | 5770.88 | 11651.9
09:30 | 5949.035 | 5723.185 | 11672.22
10:00 | 6017.05 | 5675.49 | 11692.54
10:30 | 6170.01 | 5728.465 | 11898.475
11:00 | 6322.97 | 5781.44 | 12104.41
11:30 | 6514.66 | 5859.095 | 12373.755
12:00 | 6706.35 | 5936.75 | 12643.1
12:30 | 6812.305 | 6080.1 | 12892.405
13:00 | 6918.26 | 6223.45 | 13141.71
13:30 | 6968.64 | 6215.345 | 13183.985
14:00 | 7019.02 | 6207.24 | 13226.26
14:30 | 7118.61 | 6203 | 13321.61
15:00 | 7218.2 | 6198.76 | 13416.96
15:30 | 7125.455 | 6154.075 | 13279.53
16:00 | 7032.71 | 6109.39 | 13142.1
16:30 | 7104.06 | 6014.73 | 13118.79
17:00 | 7175.41 | 5920.07 | 13095.48
17:30 | 7736.205 | 6288.635 | 14024.84
18:00 | 8297 | 6657.2 | 14954.2
18:30 | 8378.45 | 6716.7 | 15095.15
19:00 | 8459.9 | 6776.2 | 15236.1
19:30 | 8359.5 | 6827.2 | 15186.7
20:00 | 8348.5 | 6793.2 | 15141.7
20:30 | 8188.25 | 6824.2 | 15012.45 |  | Executive Engineer
21:00 | 8028 | 6855.2 | 14883.2 |  | Network Operation Division
21:30 | 8043.1 | 6838.1 | 14881.2
22:00 | 8058.2 | 6821 | 14879.2
22:30 | 8001.85 | 6788 | 14789.85
23:00 | 7945.5 | 6755 | 14700.5

## En-Curve
QF-LDC-12
Date | 25-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3457 | 1561 | 887 | 38 | 80 | 1456.56 | 220 | 4905 | 0 | 222 | 992.7 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3451 | 1535.5 | 887 | 38 | 79 | 1459.685 | 220 | 4817.5 | 0 | 191 | 979.2 | 0 | 0 | 0 | 0 | 25-10-2025
01:00 | 3445 | 1510 | 887 | 38 | 78 | 1462.81 | 220 | 4730 | 0 | 160 | 965.7 | 0 | 0 | 0 | 0
01:30 | 3406.5 | 1490 | 887 | 38 | 79 | 1467.085 | 219 | 4522 | 0 | 148.5 | 910.6 | 0 | 0 | 0 | 0 | Energy Generated | 318.5011 |  | MKWHr
02:00 | 3368 | 1470 | 887 | 38 | 80 | 1471.36 | 218 | 4314 | 0 | 137 | 855.5 | 0 | 0 | 0 | 0 | Energy not Served | 0.411 |  | MKWHr
02:30 | 3373 | 1453 | 887 | 38 | 79 | 1461.035 | 218 | 4337 | 0 | 111 | 657.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 318.9121 |  | MKWHr
03:00 | 3378 | 1436 | 887 | 38 | 78 | 1450.71 | 218 | 4360 | 0 | 85 | 459.5 | 0 | 0 | 0 | 0
03:30 | 3425 | 1435 | 887.5 | 38 | 77 | 1392.065 | 218 | 4321 | 0 | 78.5 | 381 | 0 | 0 | 0 | 0
04:00 | 3472 | 1434 | 888 | 38 | 76 | 1333.42 | 218 | 4282 | 0 | 72 | 302.5 | 0 | 0 | 0 | 0
04:30 | 3497.5 | 1430 | 888 | 38 | 72 | 1303.46 | 218 | 4205.5 | 0 | 53.5 | 239 | 0 | 0 | 0 | 0
05:00 | 3523 | 1426 | 888 | 38 | 68 | 1273.5 | 218 | 4129 | 0 | 35 | 175.5 | 0 | 0 | 0 | 0
05:30 | 3500 | 1430.5 | 888 | 38 | 68 | 1273.475 | 218 | 4037.5 | 0 | 26 | 154.75 | 0 | 0 | 0 | 0
06:00 | 3477 | 1435 | 888 | 38 | 68 | 1273.45 | 218 | 3946 | 0 | 17 | 134 | 0 | 0 | 0 | 0
06:30 | 3528 | 1432.5 | 888 | 38 | 64 | 1282.5 | 218 | 3928.5 | 39.05 | 19 | 141.5 | 0 | 0 | 2 | 0
07:00 | 3579 | 1430 | 888 | 38 | 60 | 1291.55 | 218 | 3911 | 78.1 | 21 | 149 | 0 | 0 | 4 | 0
07:30 | 3627 | 1416.5 | 888 | 38 | 61 | 1285.74 | 218.5 | 3908 | 161.835 | 31.5 | 151.5 | 0 | 0 | 2.5 | 0
08:00 | 3675 | 1403 | 888 | 38 | 62 | 1279.93 | 219 | 3905 | 245.57 | 42 | 154 | 0 | 0 | 1 | 0
08:30 | 3549 | 1314.2 | 887.5 | 38 | 61 | 1225.535 | 219 | 3902 | 326.465 | 54 | 200 | 0 | 0 | 5.5 | 0
09:00 | 3423 | 1225.4 | 887 | 38 | 60 | 1171.14 | 219 | 3899 | 407.36 | 66 | 246 | 0 | 0 | 10 | 0
09:30 | 3459.5 | 1285.4 | 887 | 38 | 64 | 1106.63 | 220 | 3804 | 501.19 | 50.5 | 246.5 | 0 | 0 | 9.5 | 0
10:00 | 3496 | 1345.4 | 887 | 38 | 68 | 1042.12 | 221 | 3709 | 595.02 | 35 | 247 | 0 | 0 | 9 | 0
10:30 | 3558 | 1381.6 | 887 | 38 | 69 | 993.235 | 221 | 3776 | 623.14 | 35 | 311 | 0 | 0 | 5.5 | 0
11:00 | 3620 | 1417.8 | 887 | 38 | 70 | 944.35 | 221 | 3843 | 651.26 | 35 | 375 | 0 | 0 | 2 | 0
11:30 | 3647 | 1437.8 | 890.5 | 38 | 69 | 954.065 | 221 | 3878.5 | 648.64 | 35 | 552.75 | 0 | 0 | 1.5 | 0
12:00 | 3674 | 1457.8 | 894 | 38 | 68 | 963.78 | 221 | 3914 | 646.02 | 35 | 730.5 | 0 | 0 | 1 | 0
12:30 | 3672 | 1477.15 | 894 | 38 | 72 | 1043.89 | 221 | 4008.5 | 589.865 | 59 | 816.5 | 0 | 0 | 0.5 | 0
13:00 | 3670 | 1496.5 | 894 | 38 | 76 | 1124 | 221 | 4103 | 533.71 | 83 | 902.5 | 0 | 0 | 0 | 0
13:30 | 3656 | 1493 | 894 | 38 | 78 | 1150 | 221 | 4116.5 | 509.985 | 129.5 | 898 | 0 | 0 | 0 | 0
14:00 | 3642 | 1489.5 | 894 | 38 | 80 | 1176 | 221 | 4130 | 486.26 | 176 | 893.5 | 0 | 0 | 0 | 0
14:30 | 3671.5 | 1491 | 893.5 | 38 | 78 | 1180 | 217.5 | 4179 | 424.11 | 195.5 | 953.5 | 0 | 0 | 0 | 0
15:00 | 3701 | 1492.5 | 893 | 38 | 76 | 1184 | 214 | 4228 | 361.96 | 215 | 1013.5 | 0 | 0 | 0 | 0
15:30 | 3646 | 1477 | 893 | 38 | 76 | 1180 | 214 | 4219 | 271.78 | 198 | 1066.75 | 0 | 0 | 0 | 0
16:00 | 3591 | 1461.5 | 893 | 38 | 76 | 1176 | 214 | 4210 | 181.6 | 181 | 1120 | 0 | 0 | 0 | 0
16:30 | 3573 | 1473.75 | 893 | 38 | 76 | 1211 | 214 | 4153.5 | 101.94 | 217.5 | 1164.6 | 0 | 0 | 2.5 | 0
17:00 | 3555 | 1486 | 893 | 38 | 76 | 1246 | 214 | 4097 | 22.28 | 254 | 1209.2 | 0 | 0 | 5 | 0
17:30 | 3682 | 1508 | 893.5 | 38 | 78 | 1350.5 | 214 | 4173.5 | 11.14 | 500.5 | 1573.2 | 0 | 0 | 2.5 | 36.5
18:00 | 3809 | 1530 | 894 | 38 | 80 | 1455 | 214 | 4250 | 0 | 747 | 1937.2 | 0 | 0 | 0 | 73
18:30 | 3747.5 | 1527.5 | 893.5 | 38 | 79 | 1451.5 | 216 | 4278 | 0 | 794.5 | 2069.15 | 0 | 0 | 0.5 | 82
19:00 | 3686 | 1525 | 893 | 38 | 78 | 1448 | 218 | 4306 | 0 | 842 | 2201.1 | 0 | 0 | 1 | 91
19:30 | 3770 | 1531 | 893 | 38 | 80 | 1471 | 218 | 4283 | 0 | 803 | 2099.7 | 0 | 0 | 0 | 71
20:00 | 3733 | 1536 | 893 | 38 | 76 | 1457 | 218 | 4278 | 0 | 813 | 2099.7 | 0 | 0 | 0 | 66
20:30 | 3647.5 | 1529 | 897 | 38 | 78 | 1456 | 219 | 4260 | 0 | 801.5 | 2086.45 | 0 | 0 | 0 | 60.5
21:00 | 3562 | 1522 | 901 | 38 | 80 | 1455 | 220 | 4242 | 0 | 790 | 2073.2 | 0 | 0 | 0 | 55
21:30 | 3595 | 1588 | 901 | 38 | 81 | 1459.5 | 220 | 4222.5 | 0 | 787 | 1989.2 | 0 | 0 | 0 | 52.5
22:00 | 3628 | 1654 | 901 | 38 | 82 | 1464 | 220 | 4203 | 0 | 784 | 1905.2 | 0 | 0 | 0 | 50
22:30 | 3707 | 1639 | 902.5 | 38 | 83 | 1467 | 219.5 | 4173 | 0 | 732 | 1828.85 | 0 | 0 | 0 | 63
23:00 | 3786 | 1624 | 904 | 38 | 84 | 1470 | 219 | 4143 | 0 | 680 | 1752.5 | 0 | 0 | 0 | 76
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 25-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 375 | 06:00 | 362 | 15:00 | Payra | 408 | 06:00 | 402 | 18:30
Ashuganj | 403 | 6:00 | 382 | 11:00 | Rahanpur | 402 | 11:00 | 383 | 18:00
Bhulta | 397 | 06:00 | 371 | 14:00 | Rampal | 397 | 06:00 | 382 | 18:00
Bibiana | 385 | 06:00 | 377 | 16:00
BIPTC | 407 | 05:00 | 397 | 18:00
Bogura | 392 | 11:00 | 369 | 18:30
Gopalganj | 391 | 06:00 | 376 | 18:30
Kaliakoir | 369 | 01:00 | 359 | 21:00
Madunaghat | 389 | 02:00 | 383 | 15:00
Meghnaghat | 376 | 06:00 | 363 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 06:00 | 214 | 11:00 | Kaliakoir | 229 | 06:00 | 217 | 04:00
AKSML | 231 | 18:30 | 223 | 12:00 | Keranigonj | 222 | 06:00 | 212 | 11:00
Aminbazar | 225 | 06:00 | 215 | 12:00 | Khulna(S) | 231 | 06:00 | 219 | 17:00
Ashuganj | 226 | 07:00 | 218 | 11:00 | Madunaghat | 231 | 19:30 | 225 | 14:00
Ashuganj-400 | 226 | 07:00 | 218 | 11:00 | Madunaghat-400 | 231 | 18:00 | 225 | 15:00
Baghabari | 234 | 06:00 | 224 | 18:00 | Maniknagar | 215 | 04:00 | 210 | 11:00
Barapukuria | 233 | 11:00 | 207 | 18:00 | Meghnaghat | 228 | 04:00 | 216 | 11:00
Barapukuria-230 | 233 | 11:00 | 207 | 18:00 | Meghnaghat-400 | 220 | 06:00 | 213 | 11:00
Barishal | 232 | 06:00 | 224 | 18:00 | Mirsorai | 228 | 19:00 | 218 | 05:00
Bheramara | 234 | 04:00 | 225 | 18:00 | Rajshahi | 233 | 04:00 | 224 | 18:30
Bhulta | 226 | 06:00 | 210 | 10:00 | Rampal | 230 | 06:00 | 217 | 18:00
Bibiana | 226 | 06:00 | 221 | 18:30 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 238 | 05:00 | 225 | 18:30 | Rampura | 225 | 06:00 | 209 | 11:00
Bogura | 239 | 11:00 | 226 | 18:00 | Shikalbaha | 230 | 17:00 | 222 | 14:00
Bogura-400 | 238 | 10:00 | 225 | 18:30 | Shyampur | 220 | 06:00 | 211 | 11:00
Borhanuddin | 235 | 06:00 | 229 | 18:00 | Siddhirganj | 216 | 05:00 | 212 | 10:00
BSRM | 227 | 19:00 | 218 | 00:00 | Sirajgonj | 237 | 05:00 | 231 | 18:00
Cumilla(N) | 220 | 05:00 | 214 | 11:00 | Sreepur | 224 | 06:00 | 218 | 15:00
Faridpur | 229 | 06:00 | 219 | 18:30 | Tongi | 225 | 04:00 | 214 | 15:00
Fenchuganj | 228 | 06:00 | 224 | 00:00
Ghorashal | 230 | 02:00 | 220 | 00:00
Ghorashal-230 | 224 | 06:00 | 211 | 10:00
Gopalganj | 230 | 06:00 | 221 | 18:00
GPH | 230 | 19:00 | 222 | 15:00
Haripur | 218 | 06:00 | 212 | 10:00
Hasnabad | 222 | 06:00 | 211 | 11:00
Hathazari | 231 | 21:00 | 223 | 13:00
Ishurdi | 237 | 05:00 | 227 | 18:30
Jhenaidah | 232 | 06:00 | 219 | 18:00
Kachua | 226 | 19:00 | 214 | 04:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 06:00 | 127 | 11:00 | Lalmonirhat | 131 | 04:00 | 120 | 18:00
Agargaon | 132 | 06:00 | 124 | 10:00 | Madanganj | 131 | 23:00 | 125 | 02:00
Agrabad | 133 | 19:00 | 126 | 14:00 | Madaripur | 133 | 05:00 | 126 | 18:00
AKS | 130 | 00:00 | 125 | 13:00 | Madartek | 138 | 06:00 | 126 | 11:00
Aminbazar | 132 | 00:00 | 126 | 12:00 | Madunaghat | 134 | 18:30 | 130 | 14:00
Amnura | 136 | 23:00 | 128 | 13:00 | Magura | 134 | 04:00 | 126 | 13:00
Ashuganj | 138 | 07:00 | 132 | 00:00 | Mahasthangarh | 132 | 06:00 | 125 | 18:00
Bagerhat | 132 | 10:00 | 116 | 18:30 | Maijdee | 129 | 12:00 | 123 | 03:00
Bajitpur | 128 | 05:00 | 123 | 01:00 | Manikganj | 131 | 04:00 | 120 | 17:00
Bakulia | 135 | 18:00 | 126 | 14:00 | Maniknagar | 131 | 03:00 | 126 | 11:00
Banani | 139 | 06:00 | 127 | 11:00 | Matarbari | 121 | 09:00 | 108 | 19:30
Bangabhaban | 132 | 06:00 | 126 | 11:00 | Matuail | 127.5 | 06:00 | 123 | 11:00
Barapukuria | 135 | 06:00 | 124 | 18:00 | Metrorail_Motijheel | 131 | 03:00 | 126 | 11:00
Barguna | 134 | 06:00 | 131 | 00:00 | Metrorail_Uttara | 135 | 04:00 | 125 | 18:00
Barishal | 133 | 09:00 | 127 | 00:00 | Millgate | 135 | 06:00 | 124 | 15:00
Barishal-230 | 132 | 05:00 | 127 | 18:00 | Mirpur | 132 | 06:00 | 125 | 12:00
Baroaulia | 132 | 00:00 | 128 | 12:00 | Mirzapur | 128 | 04:00 | 122 | 18:00
Baroirhat | 129 | 18:30 | 125 | 03:00 | Mithapukur | 132 | 06:00 | 123 | 18:30
Bashundhara | 139 | 06:00 | 125 | 18:30 | MI_Cement | 127 | 01:00 | 122 | 11:00
BashundharaCement | 131 | 23:00 | 125 | 02:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 128 | 06:00 | 123 | 18:30 | Mogbazar | 140 | 05:00 | 128 | 11:00
Benapole | 132 | 06:00 | 121 | 14:00 | Mongla | 131 | 07:00 | 118 | 18:30
Bhaluka | 127 | 19:00 | 122 | 13:00 | Motijheel | 132 | 06:00 | 126 | 11:00
Bhandaria | 132 | 09:00 | 119 | 22:00 | Muktagacha | 150 | 19:30 | 119 | 18:00
Bhangura | 134 | 06:00 | 127 | 18:30 | Munshiganj | 126 | 19:00 | 122 | 09:00
Bheramara | 138 | 04:00 | 133 | 18:30 | Muradnagar | 124 | 07:00 | 119 | 00:00
Bheramara(GK) | 138 | 04:00 | 134 | 18:00 | Mymensingh | 131 | 10:00 | 116 | 00:00
Bhulta | 122 | 01:00 | 120 | 08:00 | Naogaon | 130 | 09:00 | 121 | 18:30
Bog-Sherpur | 134 | 09:00 | 126 | 18:00 | Narail | 134 | 05:00 | 123 | 13:00
Bogura | 134 | 09:00 | 129 | 00:00 | Narinda | 131 | 03:00 | 126 | 11:00
Bogura-230 | 135 | 10:00 | 128 | 18:00 | Narshingdi | 131 | 07:00 | 116 | 11:00
Brahmanbaria | 133 | 07:00 | 126 | 00:00 | Natore | 135 | 06:00 | 130 | 00:00
Cantonment | 131 | 04:00 | 122 | 12:00 | Nawabganj | 132 | 06:00 | 123 | 13:00
Chandina | 128 | 06:00 | 125 | 00:00 | Netrakona | 121 | 04:00 | 114 | 00:00
Chandpur | 135 | 12:00 | 127 | 05:00 | New | 134 | 03:00 | 127 | 12:00
Chandraghona | 134 | 19:00 | 130 | 13:00 | Niamatpur | 136 | 05:00 | 128 | 18:00
Chapai | 135 | 09:00 | 128 | 00:00 | Noapara | 134 | 06:00 | 123 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 127 | 06:00 | 122 | 11:00 | Pabna | 136 | 05:00 | 130 | 18:00
Chauddagram | 129 | 19:00 | 123 | 00:00 | Palashbari | 131 | 06:00 | 117 | 18:00
Chhatak | 126 | 04:00 | 122 | 00:00 | Panchagarh | 138 | 22:00 | 124 | 13:00
Chowmuhani | 130 | 12:00 | 124 | 00:00 | Patiya | 132 | 19:00 | 126 | 13:00
Chuadanga | 135 | 06:00 | 122 | 18:30 | Patuakhali | 134 | 08:00 | 132 | 01:00
Coxsbazar | 120 | 17:00 | 107 | 18:00 | Payra | 136 | 06:00 | 133 | 01:00
Cumilla(N) | 128 | 19:00 | 124 | 00:00 | PHP | 129 | 19:00 | 124 | 00:00
Cumilla(S) | 131 | 01:00 | 124 | 00:00 | Postogola | 131 | 03:00 | 124 | 11:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 138 | 04:00 | 126 | 11:00
Daudkandi | 122 | 06:00 | 118 | 00:00 | Purbasadipur | 133 | 23:00 | 120 | 14:00
DhakaUniversity | 139 | 06:00 | 126 | 12:00 | Rahanpur | 137 | 09:00 | 130 | 18:00
Dhamrai | 131 | 06:00 | 123 | 11:00 | Rahanpur-400 | 138 | 10:00 | 132 | 18:00
Dhanmondi | 138 | 04:00 | 127 | 16:00 | Rahim | 127 | 05:00 | 123 | 11:00
Dohazari | 127 | 09:00 | 121 | 14:00 | Rajbari | 134 | 06:00 | 127 | 18:30
Faridpur | 135 | 06:00 | 130 | 01:00 | Rajendrapur | 131 | 19:00 | 121 | 09:00
Fatullah | 135 | 06:00 | 122 | 12:00 | Rajshahi | 135 | 06:00 | 128 | 00:00
Fenchuganj | 134 | 05:00 | 132 | 00:00 | Rajshahi-230 | 134 | 04:00 | 129 | 13:00
Feni | 130 | 19:00 | 123 | 00:00 | Ramganj | 131 | 12:00 | 124 | 00:00
Ghatail | 128 | 09:00 | 117 | 18:30 | Rampur | 132 | 18:00 | 125 | 14:00
Ghorashal | 135 | 03:00 | 127 | 18:00 | Rampura | 138 | 06:00 | 126 | 13:00
Goalpara | 136 | 06:00 | 124 | 13:00 | Rangamati | 133 | 03:00 | 130 | 11:00
Gollamari | 135 | 06:00 | 125 | 18:00 | Rangpur | 131 | 01:00 | 123 | 18:30
Gopalganj | 133 | 06:00 | 125 | 18:30 | Ruppur | 138 | 05:00 | 133 | 18:00
Gopalganj-400 | 135 | 06:00 | 128 | 18:30 | Saidpur | 132 | 04:00 | 121 | 13:00
Gulshan | 138 | 05:00 | 126 | 12:00 | Satkhira | 132 | 06:00 | 118 | 19:30
Halishahar | 133 | 18:30 | 127 | 13:00 | Satmasjid | 131 | 06:00 | 123 | 12:00
Haripur | 128 | 15:00 | 123 | 11:00 | Savar | 131 | 00:00 | 124 | 08:00
HaripurSBU | 127 | 04:00 | 124 | 12:00 | SevenRings | 134 | 06:00 | 129 | 19:00
Hasnabad | 131 | 03:00 | 124 | 11:00 | ShahCement | 127 | 06:00 | 122 | 11:00
Hathazari | 135 | 19:00 | 129 | 13:00 | Shahjadpur | 136 | 04:00 | 132 | 00:00
Ishurdi | 139 | 04:00 | 134 | 18:00 | Shahjibazar | 133 | 07:00 | 126 | 00:00
Jaldhaka | 130 | 04:00 | 120 | 18:00 | Shahmirpur | 134 | 19:00 | 127 | 13:00
Jamalpur | 130 | 09:00 | 115 | 21:00 | Shariatpur | 133 | 06:00 | 124 | 18:00
Jashore | 134 | 06:00 | 121 | 18:30 | Sherpur | 127 | 10:00 | 111 | 21:00
Jhenaidah | 137 | 05:00 | 124 | 18:30 | Shikalbaha | 123 | 18:00 | 117 | 15:00
Jhenaidah-230 | 137 | 05:00 | 128 | 18:00 | Shikalbaha-230 | 134 | 19:00 | 128 | 14:00
Joydebpur | 128 | 06:00 | 121 | 10:00 | Shitalakhya | 130 | 05:00 | 121.5 | 12:00
Joypurhat | 129 | 09:00 | 118 | 18:00 | Sholosohor | 134 | 19:00 | 130 | 11:00
Juldah | 134 | 19:00 | 127 | 14:00 | Shyampur | 133 | 00:00 | 130 | 11:00
Kabirpur | 133 | 05:00 | 122 | 18:30 | Shyampur-230 | 134 | 06:00 | 128 | 11:00
Kachua | 133 | 11:00 | 126 | 04:00 | Siddhirganj | 127 | 03:00 | 123 | 10:00
Kaliakoir | 133 | 06:00 | 126 | 11:00 | Sirajganj | 133 | 06:00 | 125 | 18:30
Kallyanpur | 132 | 04:00 | 126 | 12:00 | Sonargaon | 125 | 03:00 | 121 | 11:00
Kalurghat | 134 | 19:00 | 130 | 11:00 | Sreemongol | 132 | 07:00 | 126 | 00:00
Kamrangirchar | 131 | 07:00 | 123 | 12:00 | Sreepur | 130 | 22:00 | 125 | 18:00
Kaptai | 132 | 2:00 | 123 | 13:00 | Srinagar | 132 | 06:00 | 124 | 11:00
Kasba | 123 | 06:00 | 118 | 00:00 | SSM | 135 | 02:00 | 131 | 08:00
Kazla | 131 | 02:00 | 126 | 11:00 | Sunamganj | 125 | 06:00 | 121 | 00:00
Keranigonj | 132 | 06:00 | 124 | 12:00 | Sylhet | 130 | 07:00 | 125 | 00:00
Khagrachori | 131 | 01:00 | 128 | 13:00 | Sylhet-132 | 129 | 04:00 | 127 | 00:00
Khulna | 133 | 07:00 | 123 | 18:00 | Tangail | 126 | 09:00 | 119 | 18:00
Khulna(S) | 135 | 06:00 | 125 | 18:30 | Taraganj | 131 | 09:00 | 122 | 13:00
Khulshi | 132 | 18:00 | 125 | 13:00 | Thakurgaon | 137 | 22:00 | 123 | 08:00
Kishoreganj | 126 | 19:00 | 118 | 00:00 | TK | 134 | 19:00 | 130 | 09:00
Kodda | 130 | 20:00 | 117 | 08:00 | Tongi | 137 | 04:00 | 129 | 18:00
KSRM | 133 | 01:00 | 128 | 13:00 | Ullahpara | 134 | 05:00 | 128 | 18:00
Kulaura | 133 | 06:00 | 130 | 00:00 | Ullon | 137 | 05:00 | 126 | 13:00
Kurigram | 130 | 06:00 | 118 | 13:00 | Uttara | 131 | 00:00 | 125 | 11:00
Kushtia | 136 | 05:00 | 128 | 18:30 | UttaraNew | 135 | 04:00 | 125 | 18:00
Laksam | 132 | 12:00 | 126 | 03:00 | Zigatola | 132 | 06:00 | 123 | 13:00
Lakshmipur | 130 | 12:00 | 123 | 03:00
Lalbag | 132 | 06:00 | 122 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division