## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-07-2026 | during | 27-07-2026 | during | 27-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 327 | 352 | 412 | 412 | 325 | 325 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 140 | 148 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 45 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 296 | 300 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 37.5 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 94 | 142 | 149.36 | 149.36 | 48 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 9 | 11 | 33 | 33 | 11 | 11 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 13 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 25 | 52.19 | 52.19 | 0 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 97 | 300 | 300 | 48 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 132 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 34 | 88 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 9 | 0 | 16 | 0 | 16 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 5 | 23.29 | 23.29 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 295 | 295 | 583 | 583 | 542.7 | 542.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1492.42 | 2018.92 | 5175.93 | 5159.93 | 2001.62 | 2551.62
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 17 | 25.5 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0.17 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 208 | 211 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 91 | 98 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 35 | 74 | 40 | 72 | 40 | 72 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 34 | 0 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 2 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 48 | 90 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.68 | 0 | 2.16 | 0 | 2.16 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 284 | 300 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 54 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 106 | 107 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 43 | 87 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 60 | 146 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1190 | 1190 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 52 | 44 | 40 | 35 | 40 | 35 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 725 | 840 | 845 | 1150 | 845 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 3202.85 | 3674.86 | 3840.02 | 4203.86 | 3198.16 | 3604
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 171 | 129 | 221.25 | 221.25 | 180 | 180 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 280 | 275 | 350.01 | 350.01 | 280 | 280 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 200 | 200 | 342.01 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 24 | 24 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 21 | 15 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 137 | 142 | 163 | 163 | 145 | 145 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 175 | 172 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 140 | 150 | 84 | 80 | 84 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 93 | 99 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 88 | 115 | 115 | 34 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1423.2 | 1444.2 | 2366.44 | 2297.44 | 1264.2 | 1380.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-07-2026 | during | 27-07-2026 | during | 27-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 21.31 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.9 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 153 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 57 | 67 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 58.45 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 264.66 | 267 | 534.6 | 516.5 | 277.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 40 | 41 | 41 | 41 | 41 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 125 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 86 | 86 | 86 | 53 | 53 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 100 | 100 | 100 | 100 | 100 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 316 | 330 | 350 | 350 | 322 | 322 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 983 | 997 | 1184 | 1184 | 987 | 987
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 900 | 900 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 36 | 36 | 36 | 36 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 67 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 71 | 0 | 50 | 0 | 50 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 76 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1110 | 1166 | 1050 | 1050 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2134 | 2276 | 3356 | 3306 | 2333 | 2283
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 700 | 1050 | 1050 | 1050 | 1050 | 1050 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 28 | 100 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 1047 | 1045 | 1163.05 | 1163.05 | 1163.05 | 1163.05 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 190 | 276 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.18 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2282.18 | 2846 | 3131.05 | 3130.05 | 2977.05 | 2976.05
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 59.36 | 0 | 55 | 0 | 55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 38 | 32 | 32 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 153 | 144 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 281 | 269 | 413.79 | 413.79 | 355 | 355 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 19 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.84 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1379.06 | 1381.52 | 1469.13 | 1469.13 | 1389.13 | 1389.13 | AGC+FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 32.92 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 118 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2133.18 | 2121.72 | 3256.62 | 3035.12 | 2265.83 | 2206.33
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 70 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 190 | 185 | 0 | 0 | 190 | 190 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 85 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.9 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 95 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 22 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 160 | 0 | 148.08 | 0 | 148.08 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 472.9 | 435 | 423.08 | 242 | 480.08 | 334
System Total |  |  |  |  | 28843.2 | 29169.167 | 14388.39 | 16080.7 | 23267.74 | 23074.9 | 15784.04 | 16581.2
Forecast Scenario (27-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15030 |  | 1690.35 |  | 16800
|  |  |  | 1:00 | 14700 |  | 1642.6 |  | 16420
|  |  |  | 2:00 | 14580 |  | 1365.65 |  | 16010
|  |  |  | 3:00 | 14580 |  | 964.55 |  | 15590
|  |  |  | 4:00 | 14560 |  | 630.3 |  | 15220
|  |  |  | 5:00 | 14390 |  | 601.65 |  | 15020
|  |  |  | 6:00 | 14280 |  | 315.15 |  | 14610
|  |  |  | 7:00 | 14360 |  | 286.5 |  | 14660
|  |  |  | 8:00 | 14410 |  | 296.05 |  | 14720
|  |  |  | 9:00 | 14600 |  | 296.05 |  | 14910
|  |  |  | 10:00 | 14890 |  | 152.8 |  | 15050
|  |  |  | 11:00 | 15040 |  | 248.3 |  | 15300
|  |  |  | 12:00 | 15080 |  | 592.1 |  | 15700
|  |  |  | 13:00 | 15060 |  | 754.45 |  | 15850
|  |  |  | 14:00 | 14930 |  | 706.7 |  | 15670
|  |  |  | 15:00 | 14830 |  | 773.55 |  | 15640
|  |  |  | 16:00 | 14830 |  | 544.35 |  | 15400
|  |  |  | 17:00 | 14720 |  | 334.25 |  | 15070
|  |  |  | 18:00 | 14200 |  | 706.7 |  | 14940
|  |  |  | 18:30 | 14700 |  | 764 |  | 15500
|  |  |  | 19:00 | 15250 |  | 907.25 |  | 16200
|  |  |  | 19:30 | 16100 |  | 1241.5 |  | 17400
|  |  |  | 20:00 | 16100 |  | 1098.25 |  | 17250
|  |  |  | 21:00 | 16100 |  | 1193.75 |  | 17350
|  |  |  | 22:00 | 15800 |  | 1317.9 |  | 17180
|  |  |  | 23:00 | 15500 |  | 1403.85 |  | 16970
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 15700.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1242
Probable Maximum Demand at Evening Peak: |  |  | 17400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 357.82 MKWHr. |  | 250 | 122 | 50 | 350 | 50 | 150 | 50 | 140 | 80 | 1242
*** This report is generated digitally from Operation Information System (OIS) at 09:55 hrs on 27-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-07-2026 | [28 empty] | Date: | 26-07-2026 | [28 empty] | Date: | 26-07-2026 | [28 empty] | Date: | 26-07-2026 | [28 empty] | Date: | 26-07-2026 | [18 empty] | Date: | 26-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [18 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 17 | 45 | 144 | 97 | 55 | 35 | 0 | 0 | 0 | 147 | 310 | 0 | 0 | 308 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 87 | 230 | 62 | 0 | 18 | 17 | 39 | 17 | 25 | 25 | 0 | 222 | 106 | 2 | 775 | 132 | 0 | 50 | 25.5 | 104 | 211 | 0 | 0 | 0 | 1224 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 186 | 0 | 42 | 142 | 182 | 0 | 19 | 112 | 140 | 52.2 | 0 | 32 | 320 | 0 | 314 | 40 | 0 | 151 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7614.12 | 897 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 1190 | 0 | 0 | 0 | 1471.77 | 0 | 32 | 0 | 35 | 50 | 0 | 85 | 26 | 52.2 | 0 | 0 | 26 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 190 | 0 | 95 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 307 | 120 | 220 | 0 | 700 | 1163 | 17 | 7473.97 | 15088.09 | 103.19
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 17 | 17 | 125 | 97 | 55 | 35 | 0 | 0 | 0 | 139 | 310 | 0 | 0 | 300 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 97 | 287 | 59 | 0 | 28 | 17 | 39 | 0 | 25 | 25 | 0 | 222 | 107 | 6 | 725 | 148 | 0 | 50 | 25.5 | 101 | 213 | 0 | 0 | 0 | 1224 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 183 | 0 | 34 | 143 | 184 | 0 | 19 | 112 | 142 | 52.2 | 0 | 23 | 315 | 0 | 314 | 40 | 0 | 151 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 47 | 0 | 47 | 0 | 0 | 0 | 1 | 7539.12 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 54 | 0 | 1201 | 0 | 0 | 0 | 1477.32 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 26 | 52.2 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 190 | 0 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 307 | 120 | 220 | 0 | 500 | 1163 | 17 | 7106.52 | 14645.64 | 103.18
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 17 | 17 | 125 | 48 | 55 | 35 | 0 | 0 | 0 | 136 | 290 | 0 | 0 | 280 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 87 | 290 | 60 | 0 | 21 | 0 | 39 | 0 | 25 | 25 | 0 | 222 | 106 | 17 | 725 | 147 | 0 | 50 | 25.5 | 93 | 213 | 0 | 0 | 0 | 1224 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 183 | 0 | 0 | 143 | 185 | 0 | 19 | 108 | 136 | 52.2 | 0 | 23 | 305 | 0 | 331 | 42 | 0 | 137 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 102 | 17 | 47 | 0 | 47 | 0 | 0 | 0 | 12 | 7383.12 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 1201 | 0 | 0 | 0 | 1483.87 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 26 | 52.2 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 190 | 0 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 307 | 120 | 180 | 0 | 500 | 1163 | 17 | 7082.07 | 14465.19 | 103.18
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 17 | 17 | 125 | 48 | 55 | 0 | 0 | 0 | 0 | 150 | 290 | 0 | 0 | 310 | 0 | 0 | 0 | 143.42 | 11 | 14 | 0 | 0 | 48 | 290 | 62 | 0 | 33 | 0 | 0 | 0 | 25 | 25 | 0 | 222 | 103 | 30 | 725 | 146 | 0 | 50 | 0 | 92 | 214 | 0 | 0 | 0 | 1192 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 183 | 0 | 0 | 143 | 184 | 0 | 19 | 88 | 136 | 52.2 | 0 | 23 | 305 | 0 | 330 | 42 | 0 | 134 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 48 | 0 | 47 | 0 | 0 | 0 | 12 | 7246.62 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1191 | 0 | 0 | 0 | 1473.78 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 190 | 0 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 281 | 120 | 220 | 0 | 500 | 1125 | 17 | 6893.78 | 14140.4 | 103.18
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 17 | 17 | 125 | 48 | 55 | 0 | 0 | 0 | 0 | 144 | 300 | 0 | 0 | 293 | 0 | 0 | 0 | 143.42 | 11 | 14 | 0 | 0 | 50 | 235 | 57 | 0 | 26 | 0 | 0 | 0 | 25 | 25 | 0 | 222 | 107 | 34 | 725 | 149 | 0 | 50 | 0 | 100 | 214 | 0 | 0 | 0 | 1190 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 183 | 0 | 0 | 143 | 185 | 0 | 19 | 86 | 138 | 52.2 | 0 | 23 | 310 | 0 | 319 | 42 | 0 | 148 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 48 | 0 | 47 | 0 | 0 | 0 | 12 | 7193.62 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1150 | 0 | 0 | 0 | 1492.33 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 190 | 0 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 277 | 120 | 220 | 0 | 500 | 1100 | 17 | 6846.33 | 14039.95 | 103.18
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 17 | 17 | 125 | 48 | 55 | 0 | 0 | 0 | 0 | 149 | 305 | 0 | 0 | 305 | 0 | 0 | 0 | 143.42 | 11 | 14 | 0 | 0 | 0 | 249 | 56 | 0 | 21 | 0 | 0 | 0 | 25 | 25 | 0 | 222 | 106 | 38 | 725 | 145 | 0 | 50 | 0 | 99 | 214 | 0 | 0 | 0 | 1190 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 183 | 0 | 0 | 142 | 186 | 0 | 19 | 48 | 136 | 0 | 0 | 23 | 315 | 0 | 294 | 42 | 0 | 149 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 48 | 0 | 47 | 0 | 0 | 0 | 12 | 7060.42 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1151 | 0 | 0 | 0 | 1478.03 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 190 | 0 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 278 | 120 | 220 | 0 | 500 | 1098 | 17 | 6798.03 | 13858.45 | 103.17
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 17 | 17 | 125 | 48 | 55 | 0 | 0 | 0 | 0 | 147 | 295 | 0 | 0 | 295 | 0 | 0 | 0 | 143.42 | 11 | 14 | 0 | 0 | 0 | 155 | 56 | 0 | 25 | 0 | 0 | 0 | 25 | 25 | 0.18 | 222 | 107 | 38 | 725 | 16 | 0 | 50 | 0 | 96 | 214 | 0 | 0 | 0 | 1190 | 2 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 187 | 0 | 0 | 142 | 100 | 0 | 19 | 16 | 120 | 0 | 4 | 23 | 315 | 0 | 310 | 42 | 0 | 141 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 48 | 0.63 | 47 | 0 | 0 | 1.25 | 12 | 6703.48 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1152 | 0 | 0 | 0 | 1485.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 1.43 | 157 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0.16 | 190 | 0 | 95 | 1 | 34 | 0 | 0 | 0 | 0.2 | 6 | 0.01 | 48 | 277 | 120 | 220 | 0 | 500 | 1090 | 17 | 6679.77 | 13383.25 | 103.17
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 17 | 17 | 125 | 48 | 55 | 0 | 0 | 0 | 0 | 146 | 300 | 0 | 0 | 305 | 0 | 0 | 3 | 143.42 | 0 | 14 | 0 | 0 | 0 | 155 | 56 | 0 | 34 | 0 | 0 | 0 | 25 | 25 | 1.11 | 222 | 106 | 38 | 725 | 16 | 0 | 50 | 0 | 100 | 214 | 0 | 0 | 0 | 1193 | 3 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 180 | 0 | 0 | 141 | 100 | 0 | 19 | 14 | 120 | 0 | 12 | 23 | 310 | 0 | 318 | 42 | 0 | 150 | 4 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 0 | 48 | 2.5 | 47 | 0 | 0.3 | 6.77 | 0 | 6719.1 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33 | 1154 | 0 | 0 | 0 | 1478.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.05 | 20 | 0 | 0 | 6.51 | 158 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0.8 | 190 | 0 | 95 | 5 | 0 | 0 | 0 | 0 | 1.2 | 15 | 0.2 | 30 | 277 | 120 | 220 | 0 | 500 | 1100 | 17 | 6703.09 | 13422.19 | 103.16
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 17 | 17 | 112 | 48 | 55 | 17 | 0 | 0 | 0 | 144 | 300 | 0 | 0 | 305 | 0 | 0 | 7 | 143.42 | 0 | 14 | 0 | 0 | 0 | 155 | 49 | 0 | 42 | 0 | 0 | 0 | 25 | 25 | 2.33 | 222 | 106 | 12 | 725 | 15 | 0 | 50 | 0 | 90 | 214 | 0 | 0 | 0 | 1190 | 4 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 179 | 0 | 0 | 140 | 100 | 0 | 19 | 16 | 134 | 0 | 42 | 23 | 305 | 0 | 316 | 42 | 0 | 147 | 6 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 0 | 48 | 7.14 | 48 | 0 | 0.6 | 19.18 | 0 | 6742.67 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55 | 1150 | 0 | 0 | 0 | 1475.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.27 | 44 | 0 | 0 | 29.38 | 157 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 2.81 | 190 | 0 | 95 | 11 | 0 | 0 | 0 | 0 | 3.7 | 53 | 0.41 | 29 | 278 | 120 | 220 | 0 | 500 | 1092 | 17 | 6804.58 | 13547.25 | 103.15
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 17 | 24 | 95 | 48 | 55 | 17 | 14 | 0 | 0 | 142 | 295 | 0 | 0 | 295 | 0 | 0 | 7 | 143.42 | 0 | 14 | 0 | 0 | 0 | 155 | 54 | 0 | 45 | 0 | 0 | 17 | 25 | 25 | 2.26 | 222 | 105 | 4 | 725 | 15 | 0 | 50 | 0 | 51 | 214 | 0 | 0 | 0 | 1190 | 12 | 24 | 0 | 0 | 280 | 200 | 43 | 0 | 169 | 0 | 0 | 140 | 100 | 0 | 0 | 17 | 136 | 0 | 55 | 23 | 305 | 0 | 313 | 42 | 0 | 141 | 9 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 0 | 48 | 9.1 | 48 | 0 | 1.6 | 12.54 | 7 | 6707.92 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 61 | 1090 | 0 | 0 | 0 | 1424.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.64 | 62 | 0 | 0 | 28.99 | 158 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 2.38 | 190 | 0 | 95 | 15 | 0 | 0 | 0 | 0 | 4.5 | 72 | 0.64 | 28 | 263 | 120 | 180 | 0 | 700 | 1086 | 17 | 6887.46 | 13595.38 | 103.15
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 17 | 35 | 95 | 48 | 55 | 17 | 17 | 0 | 0 | 142 | 310 | 0 | 0 | 290 | 0 | 0 | 10 | 143.42 | 11 | 14 | 0 | 0 | 2 | 193 | 51 | 0 | 51 | 0 | 0 | 17 | 25 | 25 | 4.2 | 222 | 108 | 2 | 725 | 15 | 0 | 50 | 0 | 53 | 207 | 0 | 0 | 0 | 1175 | 4 | 24 | 0 | 0 | 280 | 200 | 43 | 0 | 171 | 0 | 0 | 139 | 117 | 0 | 17 | 84 | 136 | 0 | 64 | 21 | 315 | 0 | 310 | 41 | 0 | 150 | 12 | 14 | 0 | 53 | 0 | 0 | 0 | 100 | 0 | 57 | 20.24 | 112 | 0 | 1.8 | 29.29 | 12 | 6995.95 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 99 | 1124 | 0 | 0 | 0 | 1443.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 41.63 | 72 | 0 | 0 | 45.22 | 158 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 5.75 | 190 | 0 | 95 | 13 | 0 | 0 | 0 | 0 | 6.1 | 70 | 0.23 | 30 | 248 | 120 | 180 | 0 | 700 | 1095 | 17 | 7018.73 | 14014.68 | 103.15
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 17 | 35 | 93 | 48 | 55 | 0 | 17 | 0 | 0 | 145 | 295 | 0 | 0 | 257 | 0 | 0 | 8 | 143.42 | 10 | 14 | 0 | 0 | 38 | 244 | 50 | 0 | 64 | 0 | 29 | 17 | 25 | 25 | 4.62 | 220 | 105 | 2 | 725 | 41 | 0 | 50 | 8 | 86 | 208 | 0 | 0 | 0 | 1190 | 0.3 | 24 | 0 | 0 | 280 | 200 | 43 | 0 | 171 | 0 | 0 | 137 | 169 | 0 | 17 | 97 | 142 | 27 | 72 | 21 | 305 | 0 | 316 | 41 | 0 | 140 | 12 | 16 | 0 | 52 | 0 | 0 | 0 | 100 | 0 | 57 | 20.01 | 115 | 0 | 2.6 | 44.96 | 12 | 7241.91 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 101 | 1118 | 0 | 0 | 0 | 1400.76 | 0 | 0 | 0 | 15 | 8 | 0 | 0 | 0 | 8 | 36.56 | 118 | 0 | 0 | 38.47 | 158 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 4.54 | 190 | 0 | 95 | 18 | 0 | 0 | 0 | 0 | 3.8 | 139 | 0.65 | 28 | 199 | 100 | 180 | 0 | 700 | 1064 | 17 | 6943.78 | 14185.69 | 103.14
12:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 17 | 17 | 35 | 94 | 0 | 45 | 0 | 17 | 0 | 0 | 140 | 295 | 0 | 0 | 296 | 0 | 0 | 9 | 143.42 | 9 | 14 | 0 | 0 | 43 | 284 | 48 | 0 | 52 | 0 | 35 | 17 | 25 | 25 | 3.68 | 221 | 106 | 2 | 725 | 60 | 0 | 50 | 17 | 91 | 208 | 0 | 0 | 0 | 1190 | 0.17 | 24 | 0 | 0 | 280 | 200 | 43 | 0 | 171 | 0 | 1 | 137 | 175 | 0 | 17 | 93 | 140 | 52.2 | 69 | 21 | 305 | 0 | 316 | 41 | 0 | 140 | 12 | 16 | 0 | 52 | 0 | 0 | 0 | 101 | 0 | 57 | 21.31 | 115 | 0 | 0.9 | 58.45 | 12 | 7366.13 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 71 | 1110 | 0 | 0 | 0 | 1379.06 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 34 | 59.36 | 118 | 0 | 0 | 32.92 | 153 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 5.84 | 190 | 0 | 95 | 22 | 0 | 0 | 0 | 0 | 5.9 | 160 | 0.18 | 28 | 190 | 120 | 180 | 0 | 700 | 1047 | 17 | 7022.26 | 14388.39 | 103.14
13:00 | 0 | 34 | 5 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 52 | 93 | 0 | 55 | 0 | 17 | 0 | 0 | 142 | 300 | 0 | 17 | 299 | 0 | 0 | 19 | 143.42 | 9 | 13 | 0 | 0 | 46 | 300 | 67 | 0 | 53 | 0 | 37 | 17 | 25 | 25 | 3.37 | 221 | 104 | 2 | 725 | 86 | 0 | 50 | 17 | 103 | 208 | 0 | 0 | 0 | 1180 | 0 | 24 | 0 | 0 | 280 | 200 | 43 | 0 | 168 | 0 | 28 | 137 | 169 | 0 | 19 | 97 | 142 | 52.2 | 78 | 21 | 310 | 0 | 302 | 41 | 0 | 143 | 12 | 16 | 0 | 52 | 0 | 0 | 0 | 102 | 0 | 58 | 20.92 | 115 | 0 | 0.6 | 55.89 | 12 | 7550.4 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 66 | 1062 | 0 | 0 | 0 | 1394.15 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 52.2 | 57.9 | 110 | 0 | 0 | 40.12 | 151 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 1.6 | 190 | 0 | 95 | 19 | 0 | 0 | 0 | 0 | 8 | 163 | 0.13 | 15 | 165 | 120 | 220 | 0 | 700 | 1026 | 0 | 6950.1 | 14500.5 | 103.14
14:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 52 | 92 | 65 | 15 | 35 | 17 | 0 | 0 | 141 | 300 | 0 | 35 | 300 | 0 | 0 | 15 | 142 | 9 | 13 | 0 | 0 | 45 | 300 | 75 | 0 | 24 | 0 | 37 | 17 | 25 | 25 | 1.93 | 221 | 105 | 2 | 725 | 88 | 0 | 50 | 17 | 98 | 213 | 0 | 0 | 0 | 1190 | 0 | 24 | 0 | 0 | 280 | 200 | 43 | 0 | 169 | 0 | 34 | 138 | 176 | 0 | 19 | 95 | 158 | 52.2 | 47 | 21 | 305 | 0 | 313 | 41 | 0 | 142 | 10 | 16 | 0 | 52 | 0 | 0 | 0 | 101 | 0 | 58 | 21.31 | 115 | 0 | 2.1 | 50.61 | 12 | 7643.15 | 850 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 1063 | 0 | 0 | 0 | 1407 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 52.2 | 51.67 | 101 | 0 | 0 | 48.67 | 150 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 5.07 | 190 | 0 | 95 | 29 | 0 | 0 | 0 | 0 | 7.4 | 191 | 0.38 | 14 | 200 | 120 | 180 | 0 | 700 | 994 | 0 | 6882.39 | 14525.54 | 103.14
15:00 | 0 | 35 | 24 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 17 | 55 | 92 | 80 | 15 | 35 | 17 | 0 | 0 | 142 | 315 | 0 | 35 | 300 | 0 | 0 | 13 | 143.42 | 9 | 13 | 0 | 0 | 46 | 300 | 87 | 0 | 37 | 0 | 37 | 17 | 25 | 25 | 2.58 | 221 | 106 | 2 | 745 | 85 | 0 | 50 | 17 | 96 | 210 | 0 | 0 | 0 | 1194 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 161 | 0 | 34 | 139 | 183 | 0 | 19 | 96 | 166 | 52.2 | 45 | 20 | 315 | 0 | 318 | 41 | 0 | 146 | 9 | 16 | 0 | 52 | 0 | 0 | 0 | 101 | 0 | 58 | 15.57 | 115 | 0 | 1.8 | 38.06 | 12 | 7724.63 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 1016 | 0 | 0 | 0 | 1457.94 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 52.2 | 42.2 | 88 | 0 | 0 | 12.93 | 144 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 1.05 | 190 | 0 | 95 | 25 | 0 | 0 | 0 | 0 | 3.1 | 145 | 0.09 | 15 | 210 | 120 | 220 | 0 | 700 | 1030 | 0 | 6868.51 | 14593.14 | 103.13
16:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 70 | 78 | 81 | 15 | 35 | 60 | 0 | 0 | 138 | 300 | 0 | 35 | 300 | 0 | 0 | 9 | 143 | 9 | 0 | 0 | 0 | 16 | 300 | 84 | 0 | 49 | 0 | 66 | 17 | 25 | 25 | 2.24 | 222 | 107 | 2 | 725 | 70 | 0 | 50 | 8 | 34 | 210 | 0 | 0 | 0 | 1190 | 0 | 24 | 0 | 0 | 280 | 200 | 43 | 0 | 129 | 0 | 34 | 139 | 175 | 0 | 19 | 98 | 160 | 52.2 | 12 | 23 | 310 | 0 | 318 | 41 | 0 | 140 | 7 | 16 | 0 | 51 | 0 | 0 | 0 | 101 | 0 | 58 | 4.28 | 115 | 0 | 1.2 | 29.15 | 12 | 7473.07 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.53 | 1005 | 0 | 0 | 0 | 1455.82 | 0 | 34 | 0 | 35 | 35 | 0 | 0 | 9 | 52.2 | 25.48 | 59 | 0 | 0 | 27.54 | 144 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 2.9 | 190 | 0 | 95 | 17 | 0 | 0 | 0 | 0 | 0.8 | 83 | 0.18 | 14 | 228 | 120 | 220 | 0 | 700 | 1110 | 0 | 6878.45 | 14351.52 | 103.13
17:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 70 | 78 | 81 | 15 | 55 | 108 | 0 | 0 | 142 | 310 | 0 | 35 | 300 | 0 | 0 | 5 | 143 | 9 | 13 | 0 | 0 | 15 | 300 | 50 | 0 | 50 | 0 | 65 | 17 | 25 | 25 | 0.87 | 182 | 66 | 2 | 725 | 65 | 0 | 50 | 8 | 33 | 210 | 0 | 0 | 0 | 1195 | 0 | 24 | 0 | 0 | 280 | 200 | 43 | 0 | 127 | 0 | 34 | 139 | 182 | 11 | 19 | 51 | 150 | 43 | 10 | 13 | 315 | 0 | 318 | 41 | 0 | 143 | 3 | 16 | 0 | 51 | 0 | 0 | 0 | 101 | 0 | 58 | 5.74 | 114 | 0 | 0.8 | 13.95 | 12 | 7354.36 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 962 | 0 | 0 | 0 | 1464.71 | 0 | 35 | 0 | 35 | 35 | 0 | 0 | 20 | 52.2 | 13.87 | 31 | 0 | 0 | 13.05 | 144 | 0 | 0 | 0 | 0 | 0 | 269 | 0 | 1.4 | 186 | 0 | 70 | 7 | 40 | 0 | 0 | 0 | 2.2 | 61 | 0.1 | 15 | 282 | 120 | 220 | 0 | 700 | 1090 | 0 | 6817.53 | 14171.89 | 103.12
18:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17 | 0 | 70 | 78 | 97 | 15 | 55 | 108 | 0 | 0 | 144 | 290 | 0 | 35 | 300 | 0 | 0 | 2 | 143.42 | 9 | 13 | 0 | 0 | 16 | 300 | 50 | 0 | 51 | 0 | 71 | 17 | 25 | 50 | 0.12 | 182 | 64 | 2 | 775 | 50 | 0 | 50 | 8 | 30 | 210 | 0 | 0 | 0 | 1080 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 124 | 0 | 55 | 139 | 155 | 31 | 19 | 30 | 140 | 25 | 3 | 15 | 305 | 0 | 318 | 41 | 0 | 131 | 1 | 16 | 0 | 51 | 0 | 0 | 0 | 100 | 0 | 58 | 1.16 | 113 | 0 | 0.1 | 3.54 | 12 | 7263.34 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0.43 | 1058 | 0 | 0 | 0 | 1399.65 | 0 | 38 | 0 | 35 | 35 | 0 | 0 | 27 | 34 | 4.29 | 7 | 0 | 0 | 2.59 | 144 | 0 | 0 | 0 | 0 | 0 | 259 | 0 | 0.26 | 185 | 0 | 50 | 2 | 46 | 0 | 0 | 0 | 0.8 | 29 | 0.01 | 14 | 196 | 120 | 180 | 0 | 800 | 1078 | 0 | 6734.03 | 13997.37 | 103.12
19:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 38 | 13 | 125 | 143 | 97 | 15 | 55 | 108 | 0 | 0 | 146 | 310 | 0 | 17 | 300 | 0 | 0 | 0 | 143.42 | 9 | 13 | 0 | 0 | 15 | 300 | 51 | 0 | 33 | 34 | 71 | 22 | 25 | 50 | 0 | 182 | 71 | 2 | 840 | 55 | 0 | 50 | 8 | 33 | 210 | 0 | 0 | 0 | 1120 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 126 | 0 | 74 | 141 | 151 | 28 | 19 | 80 | 154 | 28 | 0 | 15 | 320 | 0 | 317 | 41 | 0 | 140 | 0 | 16 | 0 | 52 | 0 | 0 | 0 | 100 | 23 | 58 | 0 | 138 | 0 | 0 | 0 | 12 | 7775.42 | 899 | 0 | 0 | 20 | 0 | 38 | 0 | 0 | 50 | 0 | 67 | 0 | 1002 | 0 | 0 | 0 | 1450.22 | 0 | 38 | 0 | 35 | 45 | 0 | 100 | 27 | 43 | 0 | 0 | 25 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 257 | 0 | 0 | 184 | 0 | 90 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 243 | 120 | 180 | 0 | 1050 | 1060 | 0 | 7264.22 | 15039.64 | 103.11
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 54 | 17 | 132 | 127 | 97 | 15 | 55 | 108 | 0 | 0 | 145 | 285 | 0 | 17 | 300 | 0 | 0 | 0 | 143.42 | 10 | 13 | 0 | 0 | 35 | 300 | 51 | 0 | 34 | 34 | 71 | 54.36 | 50 | 50 | 0 | 182 | 100 | 2 | 840 | 140 | 0 | 50 | 25.5 | 90 | 210 | 0 | 0 | 0 | 1173 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 127 | 0 | 89 | 140 | 165 | 28 | 19 | 96 | 154 | 52.2 | 0 | 15 | 300 | 0 | 317 | 41 | 0 | 142 | 0 | 16 | 0 | 82 | 0 | 0 | 0 | 100 | 35 | 67 | 0 | 153 | 0 | 0 | 0 | 12 | 8198.48 | 896 | 0 | 0 | 37 | 0 | 38 | 0 | 0 | 150 | 0 | 67 | 0 | 1155 | 0 | 0 | 0 | 1449.56 | 0 | 36 | 0 | 35 | 50 | 0 | 100 | 27 | 52.2 | 0 | 0 | 25 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 257 | 0 | 0 | 185 | 0 | 95 | 0 | 74 | 0 | 100 | 0 | 0 | 0 | 0 | 48 | 277 | 120 | 220 | 0 | 1050 | 1100 | 35 | 7822.76 | 16021.24
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 54 | 0 | 132 | 143 | 97 | 15 | 55 | 108 | 0 | 0 | 140 | 295 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 11 | 13 | 0 | 0 | 45 | 300 | 59 | 0 | 39 | 34 | 71 | 47 | 50 | 50 | 0 | 222 | 97 | 6 | 840 | 133 | 0 | 50 | 22 | 84 | 209 | 0 | 0 | 0 | 1177 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 128 | 0 | 88 | 141 | 174 | 28 | 19 | 94 | 148 | 52.2 | 0 | 15 | 305 | 0 | 317 | 41 | 0 | 135 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 100 | 35 | 67 | 0 | 153 | 0 | 0 | 0 | 12 | 8267.62 | 899 | 0 | 0 | 33 | 0 | 38 | 0 | 0 | 125 | 0 | 67 | 0 | 1164 | 0 | 0 | 0 | 1394.12 | 0 | 37 | 0 | 35 | 50 | 5 | 100 | 28 | 52.2 | 0 | 0 | 25 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 258 | 0 | 0 | 185 | 0 | 95 | 0 | 80 | 0 | 120 | 0 | 0 | 0 | 0 | 90 | 256 | 120 | 220 | 0 | 1050 | 1090 | 35 | 7795.32 | 16062.94 | 103.11
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 37.5 | 5 | 132 | 142 | 97 | 15 | 55 | 108 | 0 | 0 | 148 | 295 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 11 | 13 | 0 | 0 | 87 | 300 | 90 | 0 | 44 | 34 | 74 | 54.36 | 50 | 50 | 0 | 222 | 107 | 2 | 840 | 146 | 0 | 50 | 25.5 | 98 | 211 | 0 | 0 | 0 | 1190 | 0 | 24 | 0 | 0 | 275 | 200 | 51 | 0 | 129 | 0 | 88 | 142 | 172 | 28 | 19 | 99 | 150 | 52.2 | 0 | 15 | 300 | 0 | 330 | 40 | 0 | 125 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 100 | 35 | 67 | 0 | 153 | 0 | 0 | 0 | 12 | 8401.98 | 900 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 76 | 0 | 67 | 0 | 1166 | 0 | 0 | 0 | 1381.52 | 0 | 38 | 0 | 35 | 50 | 5 | 100 | 28 | 52.2 | 0 | 0 | 19 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 269 | 0 | 0 | 185 | 0 | 95 | 0 | 85 | 0 | 70 | 0 | 0 | 0 | 0 | 100 | 276 | 120 | 220 | 0 | 1050 | 1045 | 35 | 7678.72 | 16080.7 | 103.1
22:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 35 | 26 | 132 | 138 | 97 | 15 | 35 | 54 | 0 | 0 | 150 | 295 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 11 | 14 | 0 | 0 | 86 | 300 | 91 | 0 | 52 | 34 | 65 | 54.36 | 50 | 50 | 0 | 222 | 106 | 0 | 840 | 153 | 0 | 50 | 25.5 | 94 | 212 | 0 | 0 | 0 | 1190 | 0 | 24 | 0 | 0 | 275 | 77 | 51 | 0 | 127 | 0 | 70 | 141 | 172 | 28 | 19 | 99 | 152 | 52.2 | 0 | 0 | 305 | 0 | 324 | 40 | 0 | 124 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 35 | 66 | 0 | 153 | 0 | 0 | 0 | 12 | 8152.48 | 901 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 100 | 0 | 67 | 0 | 1172 | 0 | 0 | 0 | 1382.2 | 0 | 39 | 0 | 35 | 50 | 0 | 100 | 28 | 52.2 | 0 | 0 | 19 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 269 | 0 | 0 | 185 | 0 | 95 | 0 | 80 | 0 | 70 | 0 | 0 | 0 | 0 | 99 | 276 | 120 | 220 | 0 | 1050 | 980 | 35 | 7635.4 | 15787.88 | 103.09
23:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 35 | 41 | 132 | 141 | 97 | 15 | 35 | 54 | 0 | 0 | 150 | 295 | 0 | 35 | 305 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 91 | 300 | 91 | 0 | 40 | 34 | 66 | 17 | 50 | 50 | 0 | 222 | 108 | 0 | 840 | 154 | 0 | 50 | 25.5 | 98 | 213 | 0 | 0 | 0 | 1190 | 0 | 24 | 0 | 0 | 285 | 0 | 51 | 0 | 212 | 0 | 66 | 143 | 180 | 28 | 19 | 104 | 150 | 52.2 | 0 | 0 | 310 | 0 | 323 | 40 | 0 | 141 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 35 | 68 | 0 | 153 | 0 | 0 | 0 | 12 | 8206.12 | 874 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 100 | 0 | 67 | 0 | 1191 | 0 | 0 | 0 | 1442.96 | 0 | 32 | 0 | 35 | 50 | 0 | 100 | 28 | 52.2 | 0 | 0 | 19 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 185 | 0 | 95 | 0 | 85 | 0 | 70 | 0 | 0 | 0 | 0 | 101 | 277 | 120 | 220 | 0 | 1050 | 1010 | 35 | 7727.16 | 15933.28 | 103.08
Total KWH | 0 | 862080 | 199680 | 0 | 0 | 0 | 0 | 0 | 8254800 | 0 | 0 | 263880 | 432360 | 1444032 | 2712000 | 1566927 | 898717 | 602020 | 803520 | 0 | 0 | 3469905 | 7258637 | 0 | 337916 | 7167430 | 0 | 0 | 115692 | 3476400 | 217800 | 344160 | 0 | 0 | 1047545 | 6222545 | 1557120 | 0 | 947520 | 214111 | 859584 | 400769 | 701760 | 718080 | 26383 | 4805136 | 2488200 | 227040 | 18189090.91 | 2303345 | 0 | 1215360 | 315412.2 | 2052436 | 4962942 | 0 | 0 | 0 | 28483633 | 21465 | 649018 | 0 | 0 | 7200200 | 4582000 | 1203710 | 0 | 4036000 | 0 | 700800 | 3345846 | 3926400 | 188160 | 458790 | 1827420 | 3363840 | 873787 | 466691 | 438400 | 7469000 | 0 | 7754000 | 967000 | 0 | 3396681.82 | 90219 | 376560 | 0 | 1321920 | 0 | 0 | 0 | 2402510 | 313560 | 1303200 | 132472 | 2241600 | 0 | 13950 | 336250 | 249360 | 179816777.93 | 21609455 | 0 | 0 | 146880 | 0 | 912000 | 0 | 0 | 406389 | 0 | 676224 | 546480 | 26785460 | 0 | 0 | 0 | 34123272 | 0 | 390234 | 0 | 699264 | 808128 | 11070 | 580512 | 267074 | 745368 | 396408 | 823160 | 127265 | 0 | 332496 | 3663273 | 0 | 0 | 0 | 0 | 0 | 7221164 | 0 | 35400 | 4646000 | 0 | 2215443 | 184353 | 754684 | 0 | 269640 | 0 | 43245.48 | 1185840 | 2955 | 1341792 | 6109000 | 2848000 | 5226790 | 0 | 17440000 | 26568727.27 | 421200 | 170564645.75 | 350381423.68

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14388.39 | MW | 12:00 Hr. | Energy Generated |  |  | 350.3814 |  | MKWHr.
| Day Peak Demand |  |  | 15597.39 | MW | 12:00 Hr. | Energy Unserverd |  |  | 23.901 |  | MKWHr.
| Evening Peak Generation |  |  | 16080.7 | MW | 21:00 Hr. | Energy Demand |  |  | 374.2824 |  | MKWHr.
| Evening Peak Demand |  |  | 17266.7 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 13383.25 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 685.3 |  | MMCFD
| Maximum Generation of the Day |  |  | 16080.7 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.7273 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.7127 | 0 | 13.5995 | 0 | 0 | 0.11569 | 0 | 0 | 40.428 | Gas | 95.3762 | Gas | 331533673.7444
| Chattogram Zone |  |  | 5.19 | 46.6727 | 20.0963 | 0 | 4.8051 | 0.047848 | 0 | 0.94752 | 77.7595 | Coal | 128.2219 | Coal | 865048682.1255
| Cumilla Zone |  |  | 20.8265 | 0 | 8.604 | 0 | 0 | 0.46669 | 3.3638 | 0 | 33.2611 | HFO | 55.5926 | HFO | 1023276540.288
| Mymensingh Zone |  |  | 0 | 0 | 4.1077 | 0 | 0 | 0.48267 | 0 | 0 | 4.5904 | HSD | 0.67603 | HSD | 16535541
| Sylhet Zone |  |  | 23.6877 | 0 | 0 | 0 | 0 | 0.090219 | 0 | 0 | 23.7779 | Hydro | 4.8051 | Hydro | 480513.6
| Khulna Zone |  |  | 0 | 26.7855 | 0.8231 | 0.40639 | 0 | 0.54648 | 22.5215 | 0 | 51.0829 | Solar | 4.7535 | Solar | 75873495.6184
| Barishal Zone |  |  | 8.0748 | 50.1177 | 1.763 | 0 | 0 | 0.002955 | 0 | 0 | 59.9585 | Import | 60.0086 | Import | 380814531.6
| Rajshahi Zone |  |  | 10.8844 | 0 | 3.6289 | 0 | 0 | 1.5875 | 34.1233 | 0 | 50.2241 | Wind | 0.94752 | Wind | 13938019.2
| Rangpur Zone |  |  | 0 | 4.646 | 2.9701 | 0.26964 | 0 | 1.4134 | 0 | 0 | 9.2992
| Total |  |  | 95.3762 | 128.2219 | 55.5926 | 0.67603 | 4.8051 | 4.7535 | 60.0086 | 0.94752 | 350.3814
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 331533673.7444 |  | Hydro | 480513.6
|  |  |  | Coal | 865048682.1255 |  | Solar | 75873495.6184
|  |  |  | HFO | 1023276540.288 |  | Import | 380814531.6
|  |  |  | HSD | 16535541 |  | Wind | 13938019.2
[5 empty] | Total: | 270,75,00,997 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6095 | Peak Hr Flow | 900.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51757927.27 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 34.1233 | Peak Hr Flow | 1381.52 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2168 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.3638 | Peak Hr Flow | 150.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2851 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 59.0966 | Peak Hr Flow | 2431.52 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 286 |  | 5951
|  |  |  | Chattogram |  | 0 |  | 1438
|  |  |  | Cumilla |  | 18 |  | 1448
|  |  |  | Mymensingh |  | 648 |  | 1668
|  |  |  | Sylhet |  | 84 |  | 724
|  |  |  | Khulna |  | 99 |  | 1946
|  |  |  | Barishal |  | 0 |  | 479
|  |  |  | Rajshahi |  | 0 |  | 1683
|  |  |  | Rangpur |  | 0 |  | 1152
|  |  |  | Total |  | 1135 |  | 16489
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:58 | Khulna(C )-Noapara 132kV Ckt-1 is restored.
|  | 08:58 | Khulna(C )-Noapara 132kV Ckt-1 is restored.
|  | 09:00 | Khulna(C )-Noapara 132kV Ckt-2 is restored.
|  | 09:00 | Khulna(C )-Noapara 132kV Ckt-2 is restored.
|  | 09:01 | Khulna (C) S/S TR-1 425T HT is restored.
|  | 09:02 | Khulna (C) S/S TR-1 425T LT is restored.
| 09:04 | 22:39 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 Scheduled S/D Due to Hali-khulshi ckt
line checking (R-Ph)
|  | 09:06 | Khulna (C) S/S North- West Ckt-2 is restored.
|  | 09:06 | Khulna (C) S/S North-WestCkt-1 is restored.
| 09:27 | 18:34 | Korerhat 400/230/132kV S/S ATR-3(7303T)-Three Ph LT Project Work S/D Due to DFDR work
| 09:31 | 18:33 | Korerhat 400/230/132kV S/S ATR-3(7303T)-Three Ph HT Project Work S/D Due to DFDR work
| 10:14 | 17:02 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to
Project work
| 10:14 | 17:03 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to
Project work
| 11:50 | 20:34 | Maijdee 132/33kV S/S TR-01 HT Scheduled S/D Due to BREB 33KV Red Hot Maintenance and
Others Work.
| 12:58 |  | Coxsbazar 132/33kV S/S T3 LT Tripped showing Over current really relays Due to 33kv | [7 empty] | 58.0MW load
|  |  | Teknaf feeder, 33kv Sador switching feeder O/C fault | [7 empty] | interrup.
| 15:28 | 16:26 | Sonargaon 132/33kV S/S Tr-1 LT Forced S/D Due to PBS 33KV Everest Feeder bypass blade | [7 empty] | 55.0MW load
|  |  | changing | [7 empty] | interrup.
| 15:29 | 16:25 | Sonargaon 132/33kV S/S Tr-1 HT Forced S/D Due to Due toPBS 33KV Everest feeder bypass | [7 empty] | 55.0MW load
|  |  | blade changing | [7 empty] | interrup.
| 16:32 | 17:14 | Halishahar 132/33kV S/S 425T(TR-3) HT Forced S/D Due to 33 KV PDB incomer transfomer T-03 | [7 empty] | 10.0MW load
|  |  | R-phase cable faulty work. | [7 empty] | interrup.
| 17:18 | 18:50 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to WZPDCL Maintenance work. | [7 empty] | 20.0MW load
interrup.
| 17:19 | 18:49 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to WZPDCL Maintenance work. | [7 empty] | 20.0MW load
interrup.
|  | 17:55 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
|  | 17:55 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
| 21:00 |  | Evening peak generation is 16081 MW.
| 23:56 | 00:47 | Joypurhat 132/33kV S/S Patnitola Ckt.-1 Tripped showing distance and lockout general
trip, z-1,z-2, air block, phase-A, z-2 relays Due to Thandaring
| 06:38 |  | Munshiganj 132/33kV S/S Transformer-2 HT Scheduled S/D Due to 33KV CT Change and Related
Different types of Maintenance work
| 06:38 |  | Munshiganj 132/33kV S/S Transformer-2 LT Scheduled S/D Due to 33KV CT Change and Related
Different types of Maintenance work
| 07:00 |  | Minimum generation is 13594 MW.
| 07:07 | 07:31 | Khulna (C) S/S TR-1 425T LT Tripped showing O/C relays Due to For 33kv satkhira feeder | [7 empty] | 10.0MW load
interrup.
| 07:17 |  | Keranigonj 230/132/33kV S/S TR-1 HT Scheduled S/D Due to High temperature maintenance
work.
| 07:17 |  | Keranigonj 230/132/33kV S/S TR-1 LT Scheduled S/D Due to High temperature maintenance
work.
| 07:35 |  | Khulna (C) S/S Tr-3 405T HT Scheduled S/D Due to Due to read-hot maintenance
| 07:35 |  | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to Due to read-hot maintenance
| 07:43 |  | Niamatpur 132/33kV S/S 132kV Rahanpur Ckt-1 Forced S/D Due to Rahanpur Ckt-01 & Bus-01
required to shutdown due to Rahanpur Ckt-01 ( DS Nut & Bolt ) Red-hot emergency
maintenance.
| 07:45 |  | Rahanpur 400/132kV S/S Rahanpur-Niamatpur 132 KV Line Ckt-01 Scheduled S/D Due to Due to
maintainance work at Niyamatpur side
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 352 | 8254800 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 148 | 3469905 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 898717 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7167430 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 37.5 | 263880 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 142 | 2712000 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 602020 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 337916 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 217800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 13 | 344160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 199680 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 97 | 1566927 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1444032 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 862080 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 803520 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 115692 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 5 | 432360 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 295 | 7258637 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3476400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2018.92 | 40427956
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 315412.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 21465 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1215360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 4805136 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 211 | 4962942 | plant availability zero
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 98 | 2052436 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 74 | 859584 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 214111 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 701760 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 227040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 1557120 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 26383 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 6222545 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 400769 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 107 | 2488200 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 718080 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 87 | 1047545 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 146 | 2303345 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1190 | 28483633 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 44 | 947520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 840 | 18189090.91 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 3674.86 | 77759477.11
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 129 | 4036000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 275 | 7200200 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 200 | 4582000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1203710 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 24 | 649018 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 15 | 438400 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 142 | 3345846 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 172 | 3926400 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 150 | 3363840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 873787 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 458790 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 99 | 1827420 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 188160 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 88 | 700800 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 466691 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1444.2 | 33261062
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 132472 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 153 | 2241600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1303200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 336250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 249360 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 313560 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 267 | 4590392
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 90219 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 967000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 125 | 3396681.82 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1321920 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2402510 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 376560 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7469000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 330 | 7754000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 997 | 23777890.82
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 900 | 21609455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 146880 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 676224 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 546480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 76 | 406389 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1166 | 26785460 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2276 | 51082888
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1050 | 17440000 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 100 | 1341792 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2848000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 1045 | 26568727.27 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5226790 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 421200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 6109000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2955 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2846 | 59958464.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 396408 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 390234 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 11070 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 267074 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 144 | 3663273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 269 | 7221164 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 19 | 127265 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 745368 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 580512 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 808128 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 699264 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 35400 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1381.52 | 34123272 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 332496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 823160 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2121.72 | 50224088
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 70 | 269640 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 185 | 4646000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 85 | 754684 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 43245.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 2215443 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 184353 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1185840 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 435 | 9299205.48
Eastern Grid Total |  |  |  |  | 17438.042 | 8401.98 | 179816777.93
Western Grid Total |  |  |  |  | 11731.125 | 7678.72 | 170564645.75
National Grid Total |  |  |  |  | 29169.167 | 16080.7 | 350381423.68
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10240.27 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5161.2 | MW
i) Dhaka area |  |  | 5664.77 |  | MW | i) Khulna area |  |  |  | 1847 | MW
ii) Chattogram area |  |  | 1485.5 |  | MW | ii) Barishal area |  |  |  | 478.8 | MW
iii) Cumilla area |  |  | 1430 |  | MW | iii) Rajshahi area |  |  |  | 1683.4 | MW
iv) Mymensingh area |  |  | 1020 |  | MW | iv) Rangpur area |  |  |  | 1152 | MW
v) Sylhet area |  |  | 640 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15401.47 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 143 | 10:00 | 133 | Narshingdi | 102 | 12:00 | 199 | Uttara | 103 | 13:00
2 | AKSML | 169 | 12:00 | 68 | Hasnabad | 105 | 17:00 | 134 | Natore | 170 | 21:00 | 200 | UttaraNew | 59 | 23:00
3 | Aftabnagar | 46 | 13:00 | 69 | Hathazari | 92 | 19:30 | 135 | Nawabganj | 71.6 | 08:00 | 201 | Zigatola | 98 | 13:00
4 | Agargaon | 125 | 15:00 | 70 | Hatirjheel | 97 | 15:00 | 136 | Netrakona | 103 | 23:00
5 | Agrabad | 80 | 16:00 | 71 | Ishurdi | 91 | 20:00 | 137 | New | 90 | 12:00
6 | Amnura | 31 | 00:00 | 72 | Jaldhaka | 101 | 23:00 | 138 | Niamatpur | 96 | 22:00
7 | Ashuganj | 89 | 23:00 | 73 | Jamalpur | 106 | 21:00 | 139 | Noapara | 51 | 22:00
8 | BSRM | 194 | 01:00 | 74 | Jashore | 138 | 00:00 | 140 | PHP | 10 | 12:00
9 | Bagerhat | 87 | 19:00 | 75 | Jhenaidah | 99 | 19:30 | 141 | Pabna | 106 | 20:00
10 | Bajitpur | 78 | 07:00 | 76 | Joydebpur | 136 | 19:00 | 142 | Palashbari | 138 | 02:00
11 | Bakerganj | 14.8 | 21:00 | 77 | Joypurhat | 72 | 21:00 | 143 | Panchagarh | 71 | 19:30
12 | Bakulia | 96 | 12:00 | 78 | Juldah | 17 | 12:00 | 144 | Patiya | 11 | 00:00
13 | Banani | 78.8 | 13:00 | 79 | KSRM | 38 | 15:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 18 | 10:00 | 80 | Kabirpur | 276 | 19:00 | 146 | Patuakhali | 67 | 23:00
15 | Barapukuria | 80 | 22:00 | 81 | Kachua | 100 | 22:00 | 147 | Payra | 34 | 00:00
16 | Barguna | 22 | 22:00 | 82 | Kaliganj | 41 | 21:00 | 148 | Postogola | 64 | 13:00
17 | Barishal | 106 | 12:00 | 83 | Kallyanpur | 126 | 23:00 | 149 | Pubail | 41 | 07:00
18 | Barishal-230 | 104 | 22:00 | 84 | Kalurghat | 41 | 11:00 | 150 | Purbachal | 31 | 12:00
19 | Baroaulia | 39 | 02:00 | 85 | Kamrangirchar | 80 | 13:00 | 151 | Purbasadipur | 153 | 00:00
20 | Baroirhat | 78 | 23:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 46 | 22:00
21 | Bashundhara | 217 | 15:00 | 87 | Kasba | 45 | 01:00 | 153 | Rahim | 56 | 03:00
22 | BashundharaCement | 1 | 10:00 | 88 | Kazla | 110 | 01:00 | 154 | Rajbari | 94 | 19:30
23 | Beanibazar | 82 | 19:00 | 89 | Keranigonj | 93 | 19:00 | 155 | Rajendrapur | 128 | 11:00
24 | Benapole | 75 | 20:00 | 90 | Khagrachori | 34 | 19:00 | 156 | Rajshahi | 120 | 14:00
25 | Bhaluka | 147 | 14:00 | 91 | Khulna | 60 | 19:30 | 157 | Rajshahi-230 | 110 | 21:00
26 | Bhandaria | 57 | 22:00 | 92 | Khulshi | 195 | 15:00 | 158 | Ramganj | 116 | 19:00
27 | Bhangura | 42 | 19:30 | 93 | Kishoreganj | 100 | 19:30 | 159 | Rampur | 42 | 00:00
28 | Bheramara(GK) | 73 | 22:00 | 94 | Kodda | 301 | 18:30 | 160 | Rangamati | 18 | 19:00
29 | Bhulta | 223 | 02:00 | 95 | Kulaura | 61 | 19:00 | 161 | Rangpur | 160 | 19:30
30 | Bog-Sherpur | 74 | 00:00 | 96 | Kurigram | 74 | 22:00 | 162 | Ruppur | 4.6 | 10:00
31 | Bogura | 189 | 00:00 | 97 | Kushtia | 152 | 03:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 76 | 00:00 | 98 | Laksam | 36 | 22:00 | 164 | Saidpur | 121 | 19:30
33 | Brahmanbaria | 94 | 22:00 | 99 | Lakshmipur | 48 | 19:00 | 165 | Santhia | 38 | 19:30
34 | Cantonment | 132 | 13:00 | 100 | Lalbag | 84 | 13:00 | 166 | Satkhira | 135 | 20:00
35 | Chandina | 43 | 09:00 | 101 | Lalmonirhat | 80 | 20:00 | 167 | Satmasjid | 109 | 13:00
36 | Chandpur | 88 | 00:00 | 102 | MI_Cement | 16.2 | 10:00 | 168 | Savar | 225 | 19:30
37 | Chandraghona | 35 | 20:00 | 103 | Madanganj | 47 | 20:00 | 169 | SevenRings | 17.64 | 12:00
38 | Chapai | 80 | 22:00 | 104 | Madaripur | 122 | 19:30 | 170 | ShahCement | 33 | 00:00
39 | Charfasson | 30 | 00:00 | 105 | Madartek | 85 | 21:00 | 171 | Shahjadpur | 89 | 20:00
40 | Charsaidpur | 35 | 10:00 | 106 | Madunaghat | 62 | 16:00 | 172 | Shahjibazar | 147 | 20:00
41 | Chauddagram | 79 | 22:00 | 107 | Magura | 67 | 19:30 | 173 | Shahmirpur | 53 | 18:30
42 | Chhatak | 43 | 05:00 | 108 | Mahasthangarh | 96 | 22:00 | 174 | Shariatpur | 97 | 22:00
43 | Chowmuhani | 159 | 20:00 | 109 | Maijdee | 41 | 21:00 | 175 | Sherpur | 136 | 19:00
44 | Chuadanga | 112 | 22:00 | 110 | Manikganj | 146 | 19:30 | 176 | Shikalbaha | 28.5 | 23:00
45 | Coxsbazar | 136 | 19:30 | 111 | Maniknagar | 82 | 13:00 | 177 | Shitalakhya | 78.6 | 12:00
46 | Cumilla(N) | 127 | 02:00 | 112 | Matarbari | 54 | 00:00 | 178 | Sholosohor | 49 | 19:00
47 | Cumilla(S) | 158 | 16:00 | 113 | Matuail | 82 | 16:00 | 179 | Shomvuganj | 27 | 20:00
48 | Daganbhuiyan | 36 | 23:00 | 114 | Metrorail_Motijheel | 22 | 19:00 | 180 | Shyampur | 186 | 11:00
49 | Daudkandi | 136 | 19:30 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 135 | 15:00
50 | DhakaUniversity | 98 | 13:00 | 116 | Millgate | 106 | 15:00 | 182 | Sirajganj | 132 | 20:00
51 | Dhamrai | 102 | 23:00 | 117 | Mirpur | 160 | 14:00 | 183 | Sitakunda | 34 | 19:00
52 | Dhanmondi | 125 | 13:00 | 118 | Mirsorai | 44 | 09:00 | 184 | Sonargaon | 137 | 10:00
53 | Dohazari | 108 | 20:00 | 119 | Mirzapur | 34 | 04:00 | 185 | Sreemongol | 91 | 20:00
54 | Faridpur | 185 | 21:00 | 120 | Mithapukur | 84 | 19:30 | 186 | Sreepur | 100 | 21:00
55 | Fatullah | 109 | 10:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 53.2 | 00:00
56 | Fenchuganj | 48 | 05:00 | 122 | Mogbazar | 43.1 | 13:00 | 188 | Sunamganj | 61 | 18:30
57 | Feni | 111 | 19:00 | 123 | Mongla | 39 | 16:00 | 189 | Sylhet | 135 | 19:00
58 | GPH | 8 | 02:00 | 124 | Motijheel | 53 | 13:00 | 190 | Sylhet_(South) | 82 | 19:00
59 | Ghatail | 75 | 11:00 | 125 | Muktagacha | 38 | 19:00 | 191 | TK | 26 | 19:30
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 115 | 22:00 | 192 | Tangail | 160 | 22:00
61 | Ghorashal-230 | 110 | 04:00 | 127 | Muradnagar | 54 | 21:00 | 193 | Taraganj | 30 | 19:30
62 | Goalpara | 36 | 19:30 | 128 | Mymensingh | 174 | 19:00 | 194 | Tasnim | 44 | 14:00
63 | Gollamari | 100 | 20:00 | 129 | Nabinagar | 108 | 19:00 | 195 | Thakurgaon | 125 | 21:00
64 | Gopalganj | 119 | 19:30 | 130 | Naogaon | 154 | 21:00 | 196 | Tongi | 157 | 19:30
65 | Gulshan | 124 | 13:00 | 131 | Narail | 60 | 19:30 | 197 | Ullahpara | 44 | 20:00
66 | Halishahar | 125 | 18:00 | 132 | Narinda | 82 | 13:00 | 198 | Ullon | 60 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15088.09 | 1377 |  | 16527.06
1:00 | 14645.64 | 1523 |  | 16237.64
2:00 | 14465.19 | 1210 |  | 15729.19
3:00 | 14140.4 | 943 |  | 15125.4
4:00 | 14039.95 | 889 |  | 14968.95
5:00 | 13858.45 | 782 |  | 14675.45
6:00 | 13383.25 | 721 |  | 14136.25
7:00 | 13422.19 | 660 |  | 14112.19
8:00 | 13547.25 | 671 |  | 14248.25
9:00 | 13595.38 | 648 |  | 14272.38
10:00 | 14014.68 | 717 |  | 14763.68
11:00 | 14185.69 | 726 |  | 14944.69
12:00 | 14388.39 | 1157 |  | 15597.39
13:00 | 14500.5 | 1166 |  | 15718.5
14:00 | 14525.54 | 1222 |  | 15802.54
15:00 | 14593.14 | 1290 |  | 15941.14
16:00 | 14351.52 | 1208 |  | 15613.52
17:00 | 14171.89 | 1111 |  | 15332.89
18:00 | 13997.37 | 878 |  | 14914.88
19:00 | 15039.64 | 749 |  | 15822.64
19:30 | 16021.24 | 882 |  | 16943.24
20:00 | 16062.94 | 1005 |  | 17112.94
21:00 | 16080.7 | 1135 |  | 17266.7
22:00 | 15787.88 | 992 |  | 16824.88
23:00 | 15933.28 | 1121 |  | 17104.28
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7614.12 | 7473.97 | 15088.09 | DAILY GENERATION CURVE
00:30 | 7576.62 | 7290.245 | 14866.865
01:00 | 7539.12 | 7106.52 | 14645.64 | 26-07-2026
01:30 | 7461.12 | 7094.295 | 14555.415
02:00 | 7383.12 | 7082.07 | 14465.19
02:30 | 7314.87 | 6987.925 | 14302.795
03:00 | 7246.62 | 6893.78 | 14140.4
03:30 | 7220.12 | 6870.055 | 14090.175
04:00 | 7193.62 | 6846.33 | 14039.95
04:30 | 7127.02 | 6822.18 | 13949.2
05:00 | 7060.42 | 6798.03 | 13858.45
05:30 | 6881.95 | 6738.9 | 13620.85
06:00 | 6703.48 | 6679.77 | 13383.25
06:30 | 6711.29 | 6691.43 | 13402.72
07:00 | 6719.1 | 6703.09 | 13422.19
07:30 | 6730.885 | 6753.835 | 13484.72
08:00 | 6742.67 | 6804.58 | 13547.25
08:30 | 6725.295 | 6846.02 | 13571.315
09:00 | 6707.92 | 6887.46 | 13595.38
09:30 | 6851.935 | 6953.095 | 13805.03
10:00 | 6995.95 | 7018.73 | 14014.68
10:30 | 7118.93 | 6981.255 | 14100.185
11:00 | 7241.91 | 6943.78 | 14185.69
11:30 | 7304.02 | 6983.02 | 14287.04
12:00 | 7366.13 | 7022.26 | 14388.39
12:30 | 7458.265 | 6986.18 | 14444.445
13:00 | 7550.4 | 6950.1 | 14500.5
13:30 | 7596.775 | 6916.245 | 14513.02
14:00 | 7643.15 | 6882.39 | 14525.54
14:30 | 7683.89 | 6875.45 | 14559.34
15:00 | 7724.63 | 6868.51 | 14593.14
15:30 | 7598.85 | 6873.48 | 14472.33
16:00 | 7473.07 | 6878.45 | 14351.52
16:30 | 7413.715 | 6847.99 | 14261.705
17:00 | 7354.36 | 6817.53 | 14171.89
17:30 | 7308.85 | 6775.78 | 14084.63
18:00 | 7263.34 | 6734.03 | 13997.37
18:30 | 7519.38 | 6999.125 | 14518.505
19:00 | 7775.42 | 7264.22 | 15039.64
19:30 | 8198.48 | 7822.76 | 16021.24
20:00 | 8267.62 | 7795.32 | 16062.94
20:30 | 8334.8 | 7737.02 | 16071.82 |  | Executive Engineer
21:00 | 8401.98 | 7678.72 | 16080.7 |  | Network Operation Division
21:30 | 8277.23 | 7657.06 | 15934.29
22:00 | 8152.48 | 7635.4 | 15787.88
22:30 | 8179.3 | 7681.28 | 15860.58
23:00 | 8206.12 | 7727.16 | 15933.28

## En-Curve
QF-LDC-12
Date | 26-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2735 | 1322 | 897 | 38 | 140 | 1471.77 | 222 | 5549 | 0 | 657.42 | 2037.9 | 0 | 0 | 18 | 1377 | DAILY ENERGY CURVE
00:30 | 2728.5 | 1317.5 | 897 | 38 | 141 | 1474.545 | 222 | 5429.5 | 0 | 558.42 | 2037.4 | 0 | 0 | 23 | 1450 | 26-07-2026
01:00 | 2722 | 1313 | 897 | 38 | 142 | 1477.32 | 222 | 5310 | 0 | 459.42 | 2036.9 | 0 | 0 | 28 | 1523
01:30 | 2722.5 | 1275 | 899 | 38 | 139 | 1480.595 | 222 | 5310 | 0 | 457.42 | 1987.4 | 0 | 0 | 24.5 | 1366.5 | Energy Generated | 350.3814 |  | MKWHr
02:00 | 2723 | 1237 | 901 | 38 | 136 | 1483.87 | 222 | 5310 | 0 | 455.42 | 1937.9 | 0 | 0 | 21 | 1210 | Energy not Served | 23.901 |  | MKWHr
02:30 | 2737.5 | 1265 | 900.5 | 38 | 136 | 1478.825 | 222 | 5257 | 0 | 389.42 | 1851.55 | 0 | 0 | 27 | 1076.5 | Total Energy Requirement | 374.2824 |  | MKWHr
03:00 | 2752 | 1293 | 900 | 38 | 136 | 1473.78 | 222 | 5204 | 0 | 323.42 | 1765.2 | 0 | 0 | 33 | 943
03:30 | 2737 | 1306.5 | 900 | 38 | 137 | 1483.055 | 222 | 5168 | 0 | 323.42 | 1745.7 | 0 | 0 | 29.5 | 916
04:00 | 2722 | 1320 | 900 | 38 | 138 | 1492.33 | 222 | 5132 | 0 | 323.42 | 1726.2 | 0 | 0 | 26 | 889
04:30 | 2712.5 | 1330 | 900 | 38 | 137 | 1485.18 | 222 | 5132 | 0 | 307.42 | 1661.6 | 0 | 0 | 23.5 | 835.5
05:00 | 2703 | 1340 | 900 | 38 | 136 | 1478.03 | 222 | 5132 | 0 | 291.42 | 1597 | 0 | 0 | 21 | 782
05:30 | 2707.5 | 1330 | 900 | 38 | 128 | 1481.95 | 222 | 5128 | 9.98 | 291.42 | 1361 | 0 | 0 | 23 | 751.5
06:00 | 2712 | 1320 | 900 | 38 | 120 | 1485.87 | 222 | 5124 | 19.96 | 291.42 | 1125 | 0 | 0 | 25 | 721
06:30 | 2714.5 | 1318.5 | 900.5 | 38 | 120 | 1482.1 | 222 | 5131.5 | 69.7 | 291.42 | 1085 | 0 | 0 | 29.5 | 690.5
07:00 | 2717 | 1317 | 901 | 38 | 120 | 1478.33 | 222 | 5139 | 119.44 | 291.42 | 1045 | 0 | 0 | 34 | 660
07:30 | 2712 | 1299 | 900.5 | 38 | 127 | 1476.67 | 222 | 5132 | 209.13 | 284.92 | 1045.5 | 0 | 0 | 38 | 665.5
08:00 | 2707 | 1281 | 900 | 38 | 134 | 1475.01 | 222 | 5125 | 298.82 | 278.42 | 1046 | 0 | 0 | 42 | 671
08:30 | 2690 | 1237 | 900 | 38 | 135 | 1449.66 | 222 | 5184.5 | 342.235 | 278.42 | 1051 | 0 | 0 | 43.5 | 659.5
09:00 | 2673 | 1193 | 900 | 38 | 136 | 1424.31 | 222 | 5244 | 385.65 | 278.42 | 1056 | 0 | 0 | 45 | 648
09:30 | 2657.5 | 1222 | 900 | 38 | 136 | 1434.055 | 222 | 5250.5 | 442.055 | 284.92 | 1170 | 0 | 0 | 48 | 682.5
10:00 | 2642 | 1251 | 900 | 38 | 136 | 1443.8 | 222 | 5257 | 498.46 | 291.42 | 1284 | 0 | 0 | 51 | 717
10:30 | 2591 | 1235 | 900 | 38 | 139 | 1422.28 | 221 | 5221.5 | 561.485 | 304.92 | 1408.5 | 0 | 0 | 57.5 | 721.5
11:00 | 2540 | 1219 | 900 | 38 | 142 | 1400.76 | 220 | 5186 | 624.51 | 318.42 | 1533 | 0 | 0 | 64 | 726
11:30 | 2585.5 | 1216 | 900 | 38 | 141 | 1389.91 | 220.5 | 5169 | 637.11 | 330.42 | 1601.6 | 0 | 0 | 58 | 941.5
12:00 | 2631 | 1213 | 900 | 38 | 140 | 1379.06 | 221 | 5152 | 649.71 | 342.42 | 1670.2 | 0 | 0 | 52 | 1157
12:30 | 2637.5 | 1241 | 900 | 38 | 141 | 1386.605 | 221 | 5100 | 652.62 | 337.92 | 1736.3 | 0 | 0 | 52.5 | 1161.5
13:00 | 2644 | 1269 | 900 | 38 | 142 | 1394.15 | 221 | 5048 | 655.53 | 333.42 | 1802.4 | 0 | 0 | 53 | 1166
13:30 | 2652 | 1245.5 | 875 | 38 | 150 | 1400.575 | 221 | 5055 | 638.835 | 349.71 | 1848.9 | 0 | 0 | 38.5 | 1194
14:00 | 2660 | 1222 | 850 | 38 | 158 | 1407 | 221 | 5062 | 622.14 | 366 | 1895.4 | 0 | 0 | 24 | 1222
14:30 | 2659 | 1261 | 875 | 38 | 162 | 1432.47 | 221 | 5073.5 | 543.26 | 358.71 | 1904.9 | 0 | 0 | 30.5 | 1256
15:00 | 2658 | 1300 | 900 | 38 | 166 | 1457.94 | 221 | 5085 | 464.38 | 351.42 | 1914.4 | 0 | 0 | 37 | 1290
15:30 | 2641 | 1274 | 900 | 38 | 163 | 1456.88 | 221.5 | 5116.5 | 375.84 | 369.71 | 1872.9 | 0 | 0 | 43 | 1249
16:00 | 2624 | 1248 | 900 | 38 | 160 | 1455.82 | 222 | 5148 | 287.3 | 388 | 1831.4 | 0 | 0 | 49 | 1208
16:30 | 2613 | 1265.5 | 900.5 | 38 | 155 | 1460.265 | 202 | 5144 | 232.64 | 388.5 | 1812.8 | 0 | 0 | 49.5 | 1159.5
17:00 | 2602 | 1283 | 901 | 38 | 150 | 1464.71 | 182 | 5140 | 177.98 | 389 | 1794.2 | 0 | 0 | 50 | 1111
17:30 | 2595.5 | 1247 | 901 | 38 | 145 | 1432.18 | 182 | 5156 | 117.64 | 435.71 | 1784.1 | 0 | 0 | 50.5 | 994.5
18:00 | 2589 | 1211 | 901 | 38 | 140 | 1399.65 | 182 | 5172 | 57.3 | 482.42 | 1774 | 0 | 0 | 51 | 878
18:30 | 2589 | 1234.5 | 900 | 38 | 147 | 1424.935 | 182 | 5335.5 | 28.65 | 647.92 | 1924 | 25 | 0 | 42 | 813.5
19:00 | 2589 | 1258 | 899 | 38 | 154 | 1450.22 | 182 | 5499 | 0 | 813.42 | 2074 | 50 | 0 | 33 | 749
19:30 | 2589 | 1285 | 896 | 38 | 154 | 1449.56 | 182 | 5780 | 0 | 812.42 | 2551.26 | 250 | 0 | 34 | 882
20:00 | 2590 | 1297 | 899 | 38 | 148 | 1394.12 | 222 | 5762 | 0 | 831.42 | 2597.4 | 245 | 0 | 39 | 1005
20:30 | 2601 | 1291.5 | 899.5 | 38 | 149 | 1387.82 | 222 | 5757 | 0 | 827.92 | 2661.08 | 195.5 | 0 | 41.5 | 1070
21:00 | 2612 | 1286 | 900 | 38 | 150 | 1381.52 | 222 | 5752 | 0 | 824.42 | 2724.76 | 146 | 0 | 44 | 1135
21:30 | 2546.5 | 1272 | 900.5 | 38 | 151 | 1381.86 | 222 | 5722.5 | 0 | 808.42 | 2685.51 | 158 | 0 | 48 | 1063.5
22:00 | 2481 | 1258 | 901 | 38 | 152 | 1382.2 | 222 | 5693 | 0 | 792.42 | 2646.26 | 170 | 0 | 52 | 992
22:30 | 2504.5 | 1272.5 | 887.5 | 38 | 151 | 1412.58 | 222 | 5718 | 0 | 788.42 | 2650.08 | 170 | 0 | 46 | 1056.5
23:00 | 2528 | 1287 | 874 | 38 | 150 | 1442.96 | 222 | 5743 | 0 | 784.42 | 2653.9 | 170 | 0 | 40 | 1121
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 26-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 149 | 35 | 410 | 120 | 1870 | 708 | Ishurdi-Ghorashal Ckt-1 | Export | 3843927.27
1:00 | 137 | 35 | 390 | 120 | 1672 | 678
2:00 | 149 | 42 | 388 | 120 | 1698 | 674 |  | Import | 0
3:00 | 132 | 36 | 356 | 128 | 1570 | 658
4:00 | 138 | 38 | 360 | 110 | 1598 | 650 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 143 | 38 | 380 | 124 | 1638 | 652
6:00 | 153 | 43 | 400 | 136 | 1676 | 660 |  | Import | 0
7:00 | 139 | 30 | 400 | 150 | 1716 | 700
8:00 | 172 | 50 | 490 | 188 | 1908 | 802 | Sirajganj-Sreepur Ckt-1 | Export | 2298000
9:00 | 202 | 75 | 540 | 200 | 2044 | 886
10:00 | 201 | 72 | 550 | 200 | 2100 | 900 |  | Import | 0
11:00 | 214 | 85 | 560 | 226 | 2030 | 966
12:00 | 194 | 70 | 530 | 228 | 1848 | 890 | Sirajganj-Sreepur Ckt-2 | Export | 2306000
13:00 | 180 | 60 | 490 | 220 | 1656 | 850
14:00 | 167 | 52 | 520 | 224 | 1710 | 798 |  | Import | 0
15:00 | 172 | 51 | 500 | 212 | 1732 | 802
16:00 | 172 | 50 | 480 | 164 | 1762 | 744 | Gopalganj-Aminbazar Ckt-1 | Export | 21630000
17:00 | 179 | 54 | 510 | 180 | 1882 | 802
18:00 | 175 | 54 | 460 | 140 | 1910 | 778 |  | Import | 0
18:30 | 177 | 53 | 470 | 128 | 1964 | 770
19:00 | 181 | 57 | 520 | 192 | 2008 | 778 | Gopalganj-Aminbazar Ckt-2 | Export | 21680000
19:30 | 129 | 7 | 400 | 142 | 1894 | 696
20:00 | 137 | 30 | 360 | 122 | 1854 | 694 |  | Import | 0
21:00 | 118 | 23 | 340 | 152 | 1710 | 666
22:00 | 123 | 20 | 376 | 156 | 1762 | 662 |  | Total Export | 51757927.27
23:00 | 132 | 26 | 702 | 168 | 1852 | 688 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 26-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 365 | 06:00 | 346 | 11:00 | Madunaghat | 390 | 03:00 | 384 | 10:00
Amtali | 408 | 03:00 | 403 | 19:30 | Meghnaghat | 370 | 05:00 | 351 | 11:00
Ashuganj | 389 | 6:00 | 366 | 11:00 | Payra | 411 | 04:00 | 403 | 19:30
Bhulta | 383 | 05:00 | 358 | 11:00 | Rahanpur | 395 | 18:00 | 380 | 19:30
Bibiana | 373 | 04:00 | 362 | 11:00 | Rampal | 390 | 05:00 | 374 | 19:30
BIPTC | 400 | 05:00 | 392 | 22:00
Bogura | 377 | 18:30 | 360 | 19:30
Gopalganj | 382 | 04:00 | 366 | 19:30
Kaliakoir | 352 | 06:00 | 333 | 11:00
Korerhat | 387 | 04:00 | 375 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 222 | 05:00 | 206 | 11:00 | Ishurdi | 230 | 18:30 | 206 | 19:30
AKSML | 235.3 | 04:00 | 226 | 11:00 | Jhenaidah | 222 | 18:30 | 196 | 19:30
Aminbazar | 223 | 04:00 | 207 | 11:00 | Kachua | 222 | 18:00 | 215 | 23:00
Ashuganj | 221 | 06:00 | 210 | 23:00 | Kaliakoir | 222 | 00:00 | 203 | 11:00
Ashuganj-400 | 221 | 06:00 | 210 | 23:00 | Keranigonj | 220 | 06:00 | 205 | 11:00
Baghabari | 227 | 04:00 | 213 | 19:30 | Khulna(S) | 222 | 18:30 | 207 | 19:30
Barapukuria | 222 | 11:00 | 211 | 23:00 | Korerhat | 221 | 03:00 | 216 | 10:00
Barapukuria-230 | 222 | 11:00 | 211 | 23:00 | Madunaghat | 238 | 01:00 | 232 | 19:30
Barishal | 224 | 05:00 | 216 | 19:30 | Madunaghat-400 | 239 | 01:00 | 234 | 20:00
Bheramara | 228 | 18:30 | 205 | 19:30 | Maniknagar | 218 | 05:00 | 203 | 11:00
Bhulta | 220 | 04:00 | 204 | 11:00 | Meghnaghat | 226 | 04:00 | 211 | 13:00
Bibiana | 216 | 06:00 | 208 | 11:00 | Meghnaghat-400 | 222 | 05:00 | 205 | 11:00
BIPTC | 231 | 18:30 | 205 | 19:30 | Mirsorai | 228 | 03:00 | 218 | 10:00
Bogura | 236 | 18:00 | 222 | 19:30 | Naogaon | 223 | 18:30 | 199 | 19:30
Bogura-400 | 237 | 18:30 | 225 | 23:00 | Purbasadipur | 220 | 11:00 | 208 | 23:00
Borhanuddin | 227 | 01:00 | 223 | 19:00 | Rajshahi | 228 | 18:30 | 216 | 12:00
BSRM | 223 | 04:00 | 216 | 10:00 | Rampal | 221 | 06:00 | 208 | 19:30
Charfasson | 228 | 08:00 | 223 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 220 | 01:00 | 215 | 19:30 | Rampura | 220 | 06:00 | 204 | 11:00
Cumilla(N) | 219 | 06:00 | 208 | 12:00 | Shikalbaha | 238 | 00:00 | 232 | 10:00
Faridpur | 217 | 04:00 | 208 | 19:30 | Shyampur | 221 | 06:00 | 205 | 11:00
Fenchuganj | 218 | 04:00 | 210 | 11:00 | Siddhirganj | 219 | 03:00 | 206 | 11:00
Feni | 219 | 02:00 | 213 | 10:00 | Sirajgonj | 233 | 18:00 | 224 | 19:30
Ghorashal | 220 | 01:00 | 210 | 00:00 | Sreepur | 218 | 04:00 | 208 | 19:30
Ghorashal-230 | 205 | 18:30 | 188 | 11:00 | Tongi | 207 | 04:00 | 192 | 11:00
Gopalganj | 219 | 05:00 | 209 | 19:30
GPH | 232 | 04:00 | 227 | 10:00
Haripur | 220 | 03:00 | 205 | 11:00
Hasnabad | 220 | 04:00 | 205 | 12:00
Hathazari | 234 | 18:00 | 228 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 05:00 | 124 | 11:00 | Madunaghat | 137 | 00:00 | 133 | 19:30
Agargaon | 130 | 04:00 | 119 | 11:00 | Magura | 132 | 18:00 | 113 | 19:30
Agrabad | 136 | 04:00 | 132 | 19:30 | Mahasthangarh | 132 | 11:00 | 122 | 19:30
AKS | 134 | 03:00 | 131 | 07:00 | Maijdee | 125 | 18:00 | 120 | 10:00
Aminbazar | 127 | 04:00 | 116 | 11:00 | Manikganj | 124 | 16:00 | 116 | 13:00
Amnura | 133 | 18:30 | 122 | 19:30 | Maniknagar | 129 | 05:00 | 117 | 11:00
Ashuganj | 127 | 05:00 | 120 | 12:00 | Matarbari | 132 | 13:00 | 114 | 19:30
Ashuganj-230 | 138 | 01:00 | 125 | 12:00 | Matuail | 128 | 04:00 | 119 | 11:00
Bagerhat | 125 | 07:00 | 116 | 22:00 | Metrorail_Motijheel | 129 | 04:00 | 117 | 11:00
Bajitpur | 124 | 04:00 | 115 | 13:00 | Metrorail_Uttara | 126 | 06:00 | 113 | 12:00
Bakerganj | 129 | 05:00 | 124 | 19:00 | Millgate | 127 | 03:00 | 113 | 11:00
Bakulia | 136 | 00:00 | 132 | 18:30 | Mirpur | 126 | 06:00 | 115 | 11:00
Banani | 135 | 05:00 | 124 | 11:00 | Mirzapur | 125 | 14:00 | 119 | 09:00
Bangabhaban | 128 | 05:00 | 116 | 12:00 | Mithapukur | 130 | 11:00 | 120 | 19:30
Barapukuria | 135 | 11:00 | 123 | 23:00 | MI_Cement | 130 | 06:00 | 118 | 12:00
Barguna | 130 | 04:00 | 124 | 19:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 05:00 | 124 | 19:00 | Mogbazar | 139 | 21:00 | 124 | 13:00
Barishal-230 | 130 | 04:00 | 124 | 19:00 | Mongla | 125 | 06:00 | 116 | 19:30
Baroaulia | 135 | 01:00 | 132 | 10:00 | Motijheel | 128 | 05:00 | 116 | 12:00
Baroirhat | 129 | 08:00 | 125 | 12:00 | Muktagacha | 128 | 14:00 | 113 | 00:00
Bashundhara | 136 | 06:00 | 114 | 11:00 | Munshiganj | 127 | 06:00 | 118 | 11:00
BashundharaCement | 128 | 02:00 | 119 | 11:00 | Muradnagar | 122 | 04:00 | 116 | 11:00
Beanibazar | 120 | 03:00 | 114 | 13:00 | Mymensingh | 131 | 14:00 | 107 | 15:00
Benapole | 131 | 05:00 | 109 | 19:30 | Nabinagar | 122 | 04:00 | 113 | 10:00
Bhaluka | 127 | 02:00 | 117 | 12:00 | Naogaon | 134 | 18:30 | 120 | 19:30
Bhandaria | 126 | 05:00 | 119 | 19:30 | Narail | 134 | 18:30 | 112 | 19:30
Bhangura | 131 | 05:00 | 124 | 19:30 | Narinda | 129 | 05:00 | 117 | 11:00
Bheramara | 134 | 18:30 | 120 | 19:30 | Narshingdi | 119 | 18:30 | 111 | 12:00
Bheramara(GK) | 134 | 18:30 | 121 | 19:30 | Natore | 133 | 18:30 | 122 | 19:30
Bhulta | 125 | 23:00 | 122 | 00:00 | Nawabganj | 128 | 04:00 | 120 | 11:00
Bog-Sherpur | 133 | 18:30 | 123 | 19:30 | Netrakona | 117 | 02:00 | 105 | 13:00
Bogura | 136 | 18:30 | 127 | 19:30 | New | 128 | 05:00 | 115 | 11:00
Bogura-230 | 136 | 18:00 | 126 | 19:30 | Niamatpur | 130 | 07:00 | 122 | 22:00
Brahmanbaria | 123 | 01:00 | 117 | 13:00 | Noapara | 129 | 04:00 | 116 | 07:00
Cantonment | 131 | 05:00 | 119 | 11:00 | Pabna | 132 | 18:30 | 120 | 19:30
Chandina | 125 | 04:00 | 120 | 10:00 | Palashbari | 129 | 11:00 | 117 | 19:30
Chandpur | 130 | 18:30 | 125 | 08:00 | Panchagarh | 139 | 09:00 | 128 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 137 | 06:00 | 134 | 19:30 | Patiya | 137 | 13:00 | 131 | 19:30
Chapai | 130 | 09:00 | 123 | 20:00 | Patnitala | 130 | 18:00 | 119 | 22:00
Charsaidpur | 128 | 05:00 | 119 | 11:00 | Patuakhali | 130 | 03:00 | 125 | 19:00
Chauddagram | 125 | 00:00 | 121 | 09:00 | Payra | 134 | 02:00 | 131 | 19:00
Chhatak | 120 | 02:00 | 111 | 19:00 | PHP | 128 | 04:00 | 124 | 10:00
Chowmuhani | 125 | 18:00 | 121 | 09:00 | Postogola | 131 | 05:00 | 120 | 11:00
Chuadanga | 130 | 18:00 | 113 | 19:30 | Pubail | 127 | 18:30 | 112 | 19:00
Coxsbazar | 130 | 13:00 | 118 | 19:30 | Purbachal | 135 | 04:00 | 124 | 11:00
Cumilla(N) | 125 | 01:00 | 120 | 11:00 | Purbasadipur | 134 | 19:00 | 125 | 23:00
Cumilla(S) | 129 | 06:00 | 121 | 11:00 | Rahanpur | 132 | 11:00 | 126 | 19:30
Daganbhuiyan | 126 | 04:00 | 123 | 09:00 | Rahanpur-400 | 132 | 18:00 | 127 | 19:30
Daudkandi | 121 | 01:00 | 114 | 11:00 | Rahim | 129 | 06:00 | 120 | 11:00
DhakaUniversity | 135 | 04:00 | 124 | 11:00 | Rajbari | 123 | 06:00 | 116 | 19:30
Dhamrai | 123 | 05:00 | 114 | 10:00 | Rajendrapur | 126 | 18:30 | 115 | 11:00
Dhanmondi | 135.5 | 05:00 | 123.5 | 11:00 | Rajshahi | 130 | 18:00 | 120 | 19:30
Dohazari | 134 | 13:00 | 127 | 19:30 | Rajshahi-230 | 131 | 18:00 | 118 | 19:30
Faridpur | 125 | 05:00 | 121 | 19:30 | Ramganj | 124 | 18:00 | 120 | 09:00
Fatullah | 131 | 05:00 | 119 | 10:00 | Rampur | 135 | 00:00 | 133 | 10:00
Fenchuganj | 128 | 02:00 | 123 | 14:00 | Rampura | 135 | 04:00 | 124 | 13:00
Feni | 126 | 00:00 | 123 | 11:00 | Rangamati | 136 | 01:00 | 133 | 19:30
Feni-230 | 127 | 02:00 | 124 | 00:00 | Rangpur | 129 | 11:00 | 117 | 19:30
Ghatail | 125 | 14:00 | 113 | 07:00 | Ruppur | 134 | 18:00 | 124 | 13:00
Ghorashal | 126 | 18:30 | 115 | 10:00 | Saidpur | 132 | 11:00 | 124 | 01:00
Goalpara | 132 | 04:00 | 123 | 19:30 | Santhia | 133 | 05:00 | 122 | 19:30
Gollamari | 132 | 18:30 | 123 | 19:30 | Satkhira | 129 | 18:30 | 115 | 19:30
Gopalganj | 128 | 18:00 | 121 | 19:30 | Satmasjid | 130 | 06:00 | 119 | 11:00
Gopalganj-400 | 129 | 06:00 | 123 | 19:30 | Savar | 125 | 06:00 | 113 | 11:00
Gulshan | 135 | 06:00 | 124 | 11:00 | SevenRings | 127 | 18:30 | 115 | 11:00
Halishahar | 137 | 01:00 | 133 | 10:00 | ShahCement | 128 | 05:00 | 119 | 11:00
Haripur | 128 | 04:00 | 120 | 11:00 | Shahjadpur | 135 | 19:30 | 128 | 20:00
HaripurSBU | 128 | 16:00 | 120 | 11:00 | Shahjibazar | 125 | 18:00 | 115 | 12:00
Hasnabad | 130 | 04:00 | 120 | 11:00 | Shahmirpur | 137 | 14:00 | 134 | 11:00
Hathazari | 137 | 18:00 | 134 | 01:00 | Shariatpur | 127 | 04:00 | 119 | 19:30
Hatirjheel | 135 | 04:00 | 124 | 11:00 | Sherpur | 131 | 14:00 | 107 | 01:00
Ishurdi | 135 | 18:00 | 121 | 19:30 | Shikalbaha | 127 | 05:00 | 122 | 19:30
Jaldhaka | 129 | 10:00 | 121 | 01:00 | Shikalbaha-230 | 138 | 04:00 | 135 | 10:00
Jamalpur | 134 | 14:00 | 113 | 02:00 | Shitalakhya | 130 | 06:00 | 118 | 11:00
Jashore | 131 | 06:00 | 111 | 19:30 | Sholosohor | 136 | 00:00 | 133 | 10:00
Jhenaidah | 135 | 18:30 | 117 | 19:30 | Shomvuganj | 120 | 03:00 | 110 | 13:00
Jhenaidah-230 | 136 | 18:30 | 116 | 19:30 | Shyampur | 132 | 06:00 | 119 | 11:00
Joydebpur | 126 | 18:30 | 112 | 11:00 | Shyampur-230 | 132 | 04:00 | 120 | 11:00
Joypurhat | 131 | 18:30 | 119 | 19:30 | Siddhirganj | 129 | 05:00 | 120 | 11:00
Juldah | 137 | 05:00 | 134 | 11:00 | Sirajganj | 129 | 18:30 | 119 | 19:30
Kabirpur | 126 | 06:00 | 109 | 11:00 | Sitakunda | 136 | 18:00 | 132 | 19:30
Kachua | 127 | 18:00 | 123 | 10:00 | Sonargaon | 126 | 16:00 | 117 | 11:00
Kaliakoir | 132 | 22:00 | 119 | 11:00 | Sreemongol | 123 | 02:00 | 116 | 13:00
Kaliganj | 134 | 05:00 | 115 | 19:30 | Sreepur | 128 | 18:30 | 120 | 12:00
Kallyanpur | 126 | 04:00 | 116 | 11:00 | Srinagar | 129 | 04:00 | 120 | 10:00
Kalurghat | 137 | 01:00 | 134 | 09:00 | SSM | 138 | 00:00 | 138 | 00:00
Kamrangirchar | 129 | 05:00 | 113 | 11:00 | Sunamganj | 117 | 03:00 | 110 | 13:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 122 | 02:00 | 118 | 11:00
Kasba | 122 | 04:00 | 115 | 11:00 | Sylhet_(South) | 122 | 02:00 | 116 | 19:00
Kazla | 129 | 06:00 | 116 | 12:00 | Tangail | 125 | 14:00 | 115 | 05:00
Keranigonj | 129 | 04:00 | 120 | 11:00 | Taraganj | 130 | 10:00 | 121 | 19:30
Khagrachori | 135 | 01:00 | 132 | 19:00 | Tasnim | 126 | 06:00 | 117 | 11:00
Khulna | 131 | 04:00 | 122 | 19:30 | Thakurgaon | 138 | 11:00 | 128 | 23:00
Khulna(S) | 133 | 18:30 | 123 | 19:30 | TK | 137 | 17:00 | 134 | 09:00
Khulshi | 134 | 00:00 | 130 | 19:30 | Tongi | 130 | 04:00 | 120 | 09:00
Kishoreganj | 123 | 00:00 | 114 | 13:00 | Ullahpara | 130 | 18:00 | 120 | 19:30
Kodda | 129 | 18:30 | 112 | 08:00 | Ullon | 136 | 05:00 | 123 | 13:00
Korerhat | 130 | 00:00 | 127 | 10:00 | Uttara | 125 | 06:00 | 111 | 11:00
KSRM | 136 | 00:00 | 132 | 19:30 | UttaraNew | 125 | 05:00 | 113 | 12:00
Kulaura | 127 | 02:00 | 121 | 15:00 | Zigatola | 130 | 06:00 | 121 | 11:00
Kurigram | 127 | 11:00 | 112 | 08:00
Kushtia | 130 | 18:30 | 115 | 19:30
Laksam | 126 | 18:00 | 122 | 10:00
Lakshmipur | 124 | 18:00 | 119 | 23:00
Lalbag | 129 | 04:00 | 119 | 11:00
Lalmonirhat | 125 | 11:00 | 114 | 19:30
Madanganj | 128 | 01:00 | 119 | 11:00
Madaripur | 129 | 05:00 | 123 | 21:00
Madartek | 135 | 03:00 | 123 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division