## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-10-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-10-2025 | during | 28-10-2025 | during | 28-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 350 | 350 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 208.137 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 250 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 122 | 149.36 | 149.36 | 45 | 149
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35.01 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17.8 | 20 | 24 | 24 | 24 | 24 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 293 | 293 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 145 | 134 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 105 | 105 | 52 | 105
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 126 | 162 | 162 | 108 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 325 | 310 | 584 | 584 | 584 | 584 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 160 | 160 | 70 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6655.861 | 2080.8 | 2358 | 5827.4 | 5795.4 | 4061.75 | 4276.76
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 80 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 77 | 220 | 215 | 215 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 50 | 60 | 60 | 60 | 60 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 64 | 0 | 0 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 37 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 5 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 91 | 97 | 108 | 108 | 100 | 100 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.23 | 0 | 3.25 | 0 | 3.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 20 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 35 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 38 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 112 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 160 | 159.86 | 159.86 | 144 | 144 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1112 | 1224 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 650 | 650 | 650 | 650 | 650 | 650 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4895.723 | 2317.23 | 2957.5 | 3611.97 | 3599.72 | 2999.11 | 2986.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 341 | 346 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 0 | 0 | 318.81 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 410 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 26 | 30 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 40 | 41 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 148 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 102 | 117 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 35 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 100 | 163 | 163 | 110 | 110 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 148 | 199 | 200 | 200 | 180 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 74 | 88 | 160 | 160 | 88 | 88 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 34 | 43 | 43.5 | 43.5 | 43.5 | 43.5 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 96 | 100 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 84 | 115 | 115 | 79 | 79 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 63 | 0 | 63 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1698 | 1661 | 2605.86 | 2542.86 | 1962.05 | 1908.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-10-2025 | during | 28-10-2025 | during | 28-10-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 103 | 102 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 48 | 48 | 48 | 48 | 48 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 48 | 48 | 48 | 48 | 48 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.03 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 3 | 22 | 22 | 6 | 6 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 269.03 | 218 | 377.3 | 330 | 323.8 | 276.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 70 | 70 | 70 | 70 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 151 | 143 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 80 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 162 | 162 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 0 | 0 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 7 | 10 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 310 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 312 | 312 | 325 | 325 | 330 | 330 | Load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1131 | 1131 | 1200 | 1200 | 1174 | 1174
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 905 | 903 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 372 | 382 | 410 | 410 | 410 | 410
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 70 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1148.28 | 1070 | 1182 | 0 | 0 | 1096 | 1096 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3653.28 | 2455 | 2586 | 2398 | 2318 | 2733 | 2653
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 622 | 300 | 424 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 59 | 110 | 110 | 16 | 32 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 110 | 115 | 115 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1002 | 1120 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 10 | 150 | 150 | 9 | 9 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 170 | 170 | 307 | 307 | 170 | 170 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.6 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2858 | 1802.6 | 2113 | 2147 | 2146 | 1775 | 1790
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 54.78 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 167 | 173 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 410 | 348 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.83 | 0 | 5.52 | 0 | 5.52 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1072 | 1461.29 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 55.56 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 92 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3518.96 | 1856.17 | 2368.49 | 3187.39 | 3020.87 | 2574.61 | 2408.09
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 51 | 50 | 50 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 106 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.3 | 0 | 5.8 | 0 | 5.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 95 | 95 | 95 | 95 | 95
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 94 | 0 | 171.6 | 0 | 171.6 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 950 | 234.3 | 252 | 485.4 | 278 | 415.4 | 208
System Total |  |  |  |  | 28823.2 | 28364.095 | 13844.13 | 15644.99 | 21840.32 | 21230.85 | 18018.72 | 17681.26
Forecast Scenario (28-10-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14760 |  | 0 |  | 14760
|  |  |  | 1:00 | 14170 |  | 0 |  | 14170
|  |  |  | 2:00 | 13700 |  | 0 |  | 13700
|  |  |  | 3:00 | 13330 |  | 0 |  | 13330
|  |  |  | 4:00 | 12870 |  | 0 |  | 12870
|  |  |  | 5:00 | 12600 |  | 0 |  | 12600
|  |  |  | 6:00 | 12290 |  | 0 |  | 12290
|  |  |  | 7:00 | 12420 |  | 0 |  | 12420
|  |  |  | 8:00 | 12780 |  | 0 |  | 12780
|  |  |  | 9:00 | 12880 |  | 0 |  | 12880
|  |  |  | 10:00 | 12940 |  | 0 |  | 12940
|  |  |  | 11:00 | 13450 |  | 0 |  | 13450
|  |  |  | 12:00 | 13970 |  | 0 |  | 13970
|  |  |  | 13:00 | 14290 |  | 0 |  | 14290
|  |  |  | 14:00 | 14230 |  | 0 |  | 14230
|  |  |  | 15:00 | 14250 |  | 0 |  | 14250
|  |  |  | 16:00 | 14080 |  | 0 |  | 14080
|  |  |  | 17:00 | 13940 |  | 0 |  | 13940
|  |  |  | 18:00 | 15580 |  | 0 |  | 15580
|  |  |  | 18:30 | 15600 |  | 0 |  | 15600
|  |  |  | 19:00 | 15860 |  | 0 |  | 15860
|  |  |  | 19:30 | 15720 |  | 0 |  | 15720
|  |  |  | 20:00 | 15530 |  | 0 |  | 15530
|  |  |  | 21:00 | 15480 |  | 0 |  | 15480
|  |  |  | 22:00 | 15230 |  | 0 |  | 15230
|  |  |  | 23:00 | 15030 |  | 0 |  | 15030
Probable Maximum Temperature: |  |  | 31.60°C
Probable Maximum Demand at Day Peak: |  |  | 13970.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15860.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15860.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 335.66 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:36 hrs on 28-10-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [5 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [5 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-10-2025 | [28 empty] | Date: | 27-10-2025 | [28 empty] | Date: | 27-10-2025 | [28 empty] | Date: | 27-10-2025 | [28 empty] | Date: | 27-10-2025 | [14 empty] | Date: | 27-10-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [14 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 208.137 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1148.280 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 0.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 622.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17.5 | 17 | 149 | 45 | 293 | 55 | 0 | 54 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 21 | 22 | 0 | 300 | 30 | 16 | 24 | 100 | 0 | 64 | 66 | 17 | 25 | 12 | 0 | 218 | 0 | 34 | 650 | 17 | 0 | 0 | 17 | 0 | 101 | 0 | 0 | 0 | 1155 | 0 | 51 | 132 | 107 | 393 | 350 | 0 | 44 | 0 | 28 | 31 | 103 | 130 | 0 | 19 | 15 | 80 | 25 | 0 | 29 | 315 | 0 | 312 | 0 | 67 | 157 | 10 | 0 | 81 | 30 | 0 | 16 | 162 | 17 | 48 | 48 | 126 | 0 | 0 | 6 | 7548.5 | 904 | 394 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1177 | 0 | 1463 | 0 | 0 | 0 | 0 | 70 | 0 | 50 | 0 | 8 | 0 | 0 | 18 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 483 | 1098 | 9 | 6988 | 14536.5 | 104.55
01:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17.5 | 17 | 149 | 30 | 245 | 55 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 300 | 15 | 16 | 24 | 0 | 0 | 50 | 30 | 0 | 25 | 12 | 0 | 219 | 0 | 35 | 650 | 17 | 0 | 0 | 17 | 0 | 101 | 0 | 0 | 0 | 1160 | 0 | 51 | 130 | 107 | 395 | 355 | 0 | 44 | 0 | 28 | 46 | 103 | 126 | 0 | 19 | 15 | 74 | 8 | 0 | 29 | 305 | 0 | 312 | 0 | 67 | 153 | 10 | 0 | 81 | 30 | 0 | 16 | 162 | 17 | 46 | 49 | 126 | 0 | 0 | 6 | 7188.5 | 905 | 392 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1161 | 0 | 1460 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 455 | 1095 | 9 | 6785 | 13973.5 | 104.54
02:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17.5 | 17 | 97 | 30 | 195 | 15 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 50 | 30 | 0 | 25 | 12 | 0 | 220 | 0 | 35 | 580 | 17 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 1146 | 0 | 51 | 80 | 107 | 395 | 355 | 0 | 44 | 0 | 28 | 62 | 103 | 128 | 0 | 19 | 0 | 72 | 0 | 0 | 29 | 310 | 0 | 312 | 0 | 67 | 156 | 7 | 0 | 81 | 30 | 0 | 16 | 162 | 17 | 46 | 49 | 126 | 0 | 0 | 6 | 6839.5 | 904 | 394 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1167 | 0 | 1465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 453 | 1095 | 9 | 6666 | 13505.5 | 104.53
03:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17.5 | 17 | 70 | 30 | 95 | 15 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 21 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 0 | 220 | 0 | 35 | 650 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 1165 | 0 | 51 | 40 | 107 | 395 | 355 | 0 | 44 | 0 | 28 | 38 | 103 | 85 | 0 | 19 | 0 | 70 | 0 | 0 | 0 | 315 | 0 | 312 | 0 | 67 | 152 | 7 | 0 | 81 | 30 | 0 | 16 | 161 | 17 | 46 | 49 | 142 | 0 | 0 | 6 | 6584.5 | 904 | 392 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1152 | 0 | 1465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 50 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 404 | 1090 | 9 | 6550 | 13134.5 | 104.52
04:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17.5 | 0 | 70 | 30 | 15 | 0 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 0 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 0 | 219 | 0 | 35 | 650 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 1160 | 0 | 51 | 12 | 107 | 395 | 355 | 0 | 44 | 0 | 28 | 17 | 104 | 17 | 0 | 19 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 312 | 0 | 67 | 153 | 7 | 0 | 81 | 30 | 0 | 16 | 161 | 17 | 46 | 49 | 143 | 0 | 0 | 0 | 6326.5 | 904 | 398 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 0 | 1372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 50 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 354 | 1090 | 0 | 6356 | 12682.5 | 104.51
05:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17.5 | 0 | 47 | 30 | 0 | 0 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 0 | 216 | 0 | 35 | 650 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 1155 | 0 | 51 | 0 | 107 | 396 | 355 | 0 | 44 | 0 | 28 | 0 | 104 | 15 | 0 | 19 | 0 | 68 | 0 | 0 | 0 | 310 | 0 | 312 | 0 | 67 | 155 | 7 | 0 | 81 | 30 | 0 | 16 | 161 | 17 | 48 | 49 | 143 | 0 | 0 | 0 | 6260 | 904 | 398 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 1277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 306 | 1094 | 0 | 6166 | 12426 | 104.5
06:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17.5 | 0 | 34 | 30 | 0 | 0 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 0 | 218 | 0 | 38 | 650 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 1166 | 0 | 51 | 0 | 107 | 395 | 353 | 0 | 45 | 0 | 28 | 0 | 104 | 15 | 0 | 19 | 0 | 64 | 0 | 0 | 0 | 305 | 0 | 312 | 0 | 67 | 154 | 7 | 0 | 81 | 30 | 0 | 16 | 161 | 17 | 48 | 48 | 143 | 0 | 0 | 0 | 6190 | 904 | 401 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1049 | 0 | 1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 303 | 1022 | 0 | 5979 | 12169 | 104.49
07:00 | 0 | 52 | 12 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 12 | 76 | 30 | 0 | 35 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 4 | 17 | 13.5 | 22 | 0 | 300 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 25 | 12 | 0.49 | 218 | 0 | 36 | 650 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 1166 | 5 | 51 | 0 | 107 | 395 | 355 | 0 | 45 | 0 | 28 | 16 | 103 | 81 | 0 | 19 | 0 | 56 | 5 | 13 | 0 | 320 | 0 | 312 | 0 | 67 | 160 | 7 | 0 | 81 | 30 | 0 | 16 | 161 | 17 | 48 | 49 | 110 | 0 | 3.76 | 0 | 6546.75 | 904 | 403 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 960 | 0 | 977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.59 | 11 | 0 | 0 | 4.53 | 166 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0.38 | 0 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0.6 | 12 | 0.07 | 0 | 170 | 110 | 220 | 0 | 302 | 996 | 0 | 5698.17 | 12244.92 | 104.48
08:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 17 | 141 | 45 | 45 | 55 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 13 | 35 | 13.5 | 22 | 0 | 300 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 25 | 12 | 1.39 | 217 | 0 | 10 | 650 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 1165 | 11 | 51 | 5 | 107 | 396 | 350 | 0 | 44 | 0 | 28 | 34 | 101 | 103 | 0 | 19 | 0 | 58 | 16 | 34 | 0 | 310 | 0 | 312 | 0 | 67 | 149 | 7 | 0 | 77 | 30 | 0 | 16 | 161 | 17 | 48 | 49 | 110 | 1 | 21.04 | 0 | 6765.93 | 905 | 397 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29 | 940 | 0 | 980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.47 | 29 | 0 | 0 | 13.57 | 159 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 1.17 | 0 | 50 | 0 | 4 | 0 | 0 | 0 | 0 | 2.2 | 58 | 0.21 | 0 | 170 | 110 | 220 | 0 | 305 | 998 | 0 | 5785.62 | 12551.55 | 104.47
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 17 | 97 | 45 | 45 | 55 | 5 | 35 | 0 | 280 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 20 | 35 | 13.3 | 22 | 0 | 300 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 25 | 12 | 2.27 | 220 | 0 | 3 | 650 | 0 | 0 | 0 | 1 | 0 | 45 | 0 | 0 | 0 | 1115 | 15 | 51 | 50 | 107 | 355 | 300 | 0 | 44 | 0 | 28 | 34 | 100 | 96 | 0 | 19 | 0 | 58 | 16 | 52 | 20 | 310 | 0 | 312 | 0 | 67 | 146 | 7 | 0 | 78 | 30 | 0 | 17 | 161 | 17 | 49 | 48 | 110 | 1 | 31.46 | 0 | 6690.03 | 905 | 405 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 51 | 942 | 0 | 965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.45 | 63 | 0 | 0 | 46.33 | 160 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 3.68 | 0 | 52 | 35 | 10 | 15 | 0 | 0 | 0 | 1.7 | 112 | 0.37 | 0 | 170 | 110 | 180 | 0 | 304 | 1002 | 0 | 5941.53 | 12631.56 | 104.46
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 17 | 97 | 45 | 115 | 55 | 17 | 35 | 0 | 280 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 25 | 52 | 13.3 | 22 | 0 | 310 | 0 | 0 | 38 | 140 | 0 | 0 | 0 | 0 | 25 | 12 | 2.89 | 221 | 0 | 2 | 650 | 0 | 0 | 0 | 8 | 0 | 54 | 0 | 0 | 0 | 1052 | 18 | 51 | 50 | 107 | 350 | 342 | 0 | 44 | 0 | 28 | 34 | 98 | 96 | 0 | 19 | 0 | 60 | 16 | 63 | 21 | 315 | 0 | 312 | 0 | 67 | 149 | 7 | 0 | 78 | 30 | 0 | 17 | 162 | 17 | 49 | 48 | 110 | 2 | 43.86 | 0 | 6813.05 | 905 | 389 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 907 | 0 | 960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.29 | 81 | 0 | 0 | 47.03 | 161 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 3.33 | 0 | 52 | 35 | 24 | 34 | 0 | 0 | 0 | 4.8 | 155 | 0.51 | 0 | 170 | 110 | 220 | 0 | 250 | 955 | 0 | 5999.96 | 12813.01 | 104.45
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 99 | 45 | 268 | 55 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 26 | 52 | 17 | 22 | 0 | 320 | 0 | 0 | 59 | 100 | 0 | 0 | 0 | 0 | 25 | 12 | 3.2 | 221 | 0 | 2 | 650 | 17 | 0 | 0 | 8 | 0 | 77 | 0 | 0 | 0 | 1057 | 19 | 43 | 72 | 110 | 393 | 345 | 0 | 40 | 0 | 26 | 34 | 99 | 112 | 0 | 19 | 6 | 73 | 16 | 67 | 28 | 315 | 0 | 312 | 0 | 67 | 158 | 7 | 0 | 77 | 30 | 0 | 17 | 162 | 17 | 49 | 48 | 103 | 2 | 44.14 | 1 | 7127.34 | 904 | 389 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 1021 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.81 | 87 | 0 | 0 | 55.73 | 168 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 4.7 | 0 | 51 | 35 | 32 | 34 | 0 | 0 | 0 | 6 | 177 | 0.56 | 0 | 170 | 110 | 220 | 0 | 250 | 984 | 0 | 6197.8 | 13325.14 | 104.43
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 145 | 45 | 293 | 55 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 28 | 52 | 17.8 | 22 | 0 | 325 | 0 | 0 | 91 | 80 | 0 | 0 | 0 | 0 | 12 | 12 | 3.23 | 222 | 0 | 5 | 650 | 17 | 0 | 0 | 17 | 0 | 77 | 0 | 0 | 0 | 1112 | 19 | 51 | 102 | 148 | 393 | 341 | 0 | 40 | 0 | 26 | 34 | 98 | 148 | 0 | 17 | 96 | 74 | 34 | 66 | 30 | 305 | 0 | 312 | 0 | 67 | 151 | 7 | 0 | 80 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 103 | 2 | 45.03 | 6 | 7496.06 | 905 | 372 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70 | 1070 | 0 | 1072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.78 | 92 | 0 | 0 | 55.56 | 167 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 4.83 | 0 | 48 | 35 | 19 | 34 | 0 | 0 | 0 | 4.3 | 94 | 0.6 | 0 | 170 | 110 | 220 | 0 | 300 | 1002 | 0 | 6348.07 | 13844.13 | 104.41
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 135 | 45 | 293 | 55 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 26 | 52 | 18 | 22 | 0 | 320 | 0 | 0 | 104 | 0 | 1 | 0 | 0 | 0 | 12 | 12 | 2.98 | 222 | 0 | 12 | 650 | 17 | 0 | 0 | 17 | 0 | 161 | 0 | 0 | 0 | 1110 | 19 | 51 | 93 | 160 | 355 | 342 | 0 | 40 | 0 | 26 | 34 | 97 | 179 | 0 | 17 | 100 | 84 | 34 | 64 | 33 | 315 | 0 | 312 | 0 | 67 | 150 | 7 | 0 | 79 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 102 | 2 | 39.42 | 6 | 7514.4 | 904 | 387 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 78 | 1097 | 0 | 1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.35 | 89 | 0 | 0 | 52.41 | 183 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.53 | 0 | 50 | 35 | 33 | 34 | 0 | 0 | 0 | 3.5 | 163 | 0.55 | 0 | 170 | 110 | 220 | 0 | 301 | 1040 | 0 | 6600.34 | 14114.74 | 104.39
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 149 | 45 | 293 | 55 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 21 | 52 | 18.4 | 19 | 0 | 328 | 0 | 0 | 100 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 2.42 | 222 | 0 | 6 | 650 | 17 | 0 | 0 | 17 | 0 | 176 | 0 | 0 | 0 | 1110 | 16 | 51 | 88 | 0 | 393 | 337 | 0 | 41 | 0 | 26 | 44 | 96 | 180 | 0 | 17 | 104 | 72 | 34 | 53 | 26 | 310 | 0 | 312 | 0 | 67 | 154 | 7 | 0 | 80 | 30 | 0 | 17 | 163 | 17 | 48 | 48 | 102 | 1 | 17.61 | 6 | 7362.43 | 904 | 387 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 65 | 1115 | 0 | 1230.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.5 | 62 | 0 | 0 | 34.62 | 187 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.51 | 0 | 50 | 35 | 12 | 34 | 0 | 0 | 0 | 2.5 | 168 | 0.45 | 0 | 170 | 110 | 220 | 0 | 300 | 1070 | 0 | 6653.59 | 14016.02 | 104.37
15:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 149 | 45 | 276 | 55 | 35 | 72 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 15 | 52 | 18.4 | 22 | 0 | 340 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.58 | 222 | 0 | 2 | 650 | 17 | 0 | 0 | 17 | 0 | 214 | 0 | 0 | 0 | 1120 | 12 | 51 | 83 | 0 | 400 | 337 | 0 | 42 | 0 | 30 | 51 | 97 | 182 | 0 | 17 | 100 | 70 | 43 | 37 | 33 | 315 | 0 | 312 | 0 | 67 | 155 | 7 | 0 | 80 | 30 | 0 | 17 | 163 | 17 | 48 | 48 | 102 | 1 | 12.95 | 6 | 7380.93 | 903 | 386 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 1100 | 0 | 1344.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.42 | 50 | 0 | 0 | 21.43 | 181 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 2.28 | 0 | 50 | 35 | 12 | 34 | 0 | 0 | 0 | 1.7 | 106 | 0.31 | 0 | 170 | 110 | 220 | 0 | 301 | 1072 | 0 | 6597.56 | 13978.49 | 104.35
16:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 134 | 45 | 276 | 55 | 55 | 72 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 8 | 52 | 19 | 22 | 0 | 319 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0.1 | 221 | 0 | 4 | 650 | 17 | 0 | 0 | 17 | 0 | 211 | 0 | 0 | 0 | 1110 | 6 | 51 | 80 | 0 | 400 | 340 | 0 | 41 | 0 | 30 | 51 | 98 | 180 | 0 | 12 | 110 | 72 | 43 | 17 | 33 | 320 | 0 | 312 | 0 | 67 | 155 | 7 | 0 | 80 | 30 | 0 | 17 | 163 | 17 | 48 | 48 | 101 | 0 | 11.09 | 6 | 7329.19 | 903 | 386 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 1150 | 0 | 1334.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.87 | 20 | 0 | 0 | 11.73 | 172 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 1.03 | 0 | 50 | 35 | 5 | 34 | 0 | 0 | 0 | 1.3 | 38 | 0.14 | 0 | 170 | 110 | 220 | 0 | 302 | 1070 | 0 | 6485.05 | 13814.24 | 104.33
17:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 27 | 134 | 72 | 276 | 55 | 55 | 90 | 0 | 280 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 1 | 52 | 19 | 22 | 0 | 310 | 1 | 10 | 102 | 0 | 0 | 19 | 0 | 1 | 12 | 12 | 0.02 | 221 | 0 | 9 | 652 | 35 | 0 | 0 | 17 | 0 | 212 | 0 | 0 | 0 | 1085 | 0 | 51 | 85 | 0 | 405 | 344 | 0 | 29 | 0 | 30 | 51 | 100 | 180 | 0 | 0 | 102 | 68 | 43 | 2 | 35 | 315 | 0 | 312 | 0 | 67 | 155 | 7 | 0 | 80 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 102 | 0 | 0.96 | 6 | 7348.98 | 903 | 384 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1125 | 0 | 1310.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 4 | 12 | 0 | 1.47 | 170 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0.14 | 0 | 50 | 35 | 1 | 34 | 0 | 0 | 0 | 0 | 3 | 0.02 | 0 | 170 | 110 | 220 | 0 | 301 | 1072 | 0 | 6353.28 | 13702.26 | 104.31
18:00 | 0 | 40 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 35 | 134 | 122 | 293 | 55 | 55 | 126 | 0 | 280 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 330 | 36 | 17 | 90 | 0 | 0 | 64 | 35 | 19 | 37 | 38 | 0 | 219 | 0 | 9 | 650 | 160 | 0 | 0 | 17 | 0 | 220 | 0 | 0 | 0 | 1224 | 0 | 51 | 112 | 0 | 410 | 349 | 0 | 37 | 0 | 30 | 54 | 100 | 184 | 0 | 12 | 100 | 86 | 43 | 0 | 35 | 320 | 0 | 312 | 0 | 67 | 153 | 8 | 0 | 80 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 102 | 0 | 0 | 6 | 8162 | 903 | 354 | 0 | 30 | 24 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 1418.45 | 0 | 49 | 0 | 35 | 28 | 0 | 88 | 15 | 52.2 | 0 | 0 | 25 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 50 | 92 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 170 | 110 | 180 | 0 | 500 | 1112 | 10 | 7159.65 | 15321.65 | 104.29
19:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 35 | 134 | 122 | 293 | 55 | 35 | 126 | 0 | 280 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 310 | 112 | 20 | 97 | 0 | 0 | 64 | 50 | 35 | 37 | 38 | 0 | 220 | 0 | 5 | 650 | 160 | 0 | 0 | 25.5 | 0 | 220 | 0 | 0 | 0 | 1224 | 0 | 51 | 117 | 0 | 410 | 346 | 0 | 41 | 0 | 30 | 84 | 100 | 199 | 0 | 17 | 100 | 88 | 43 | 0 | 35 | 310 | 0 | 312 | 0 | 67 | 143 | 10 | 0 | 80 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 102 | 0 | 0 | 3 | 8325.5 | 903 | 382 | 0 | 41 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1182 | 0 | 1461.29 | 0 | 48 | 0 | 35 | 108 | 0 | 88 | 30 | 52.2 | 0 | 0 | 25 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 51 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 170 | 110 | 220 | 0 | 424 | 1120 | 10 | 7319.49 | 15644.99 | 104.28
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 35 | 134 | 122 | 293 | 55 | 35 | 126 | 0 | 280 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 310 | 115 | 20 | 97 | 0 | 0 | 64 | 64 | 35 | 37 | 38 | 0 | 220 | 0 | 9 | 650 | 108 | 0 | 0 | 25.5 | 0 | 220 | 0 | 0 | 0 | 1224 | 0 | 51 | 122 | 0 | 395 | 348 | 0 | 41 | 0 | 31 | 90 | 100 | 199 | 0 | 17 | 100 | 76 | 43 | 0 | 41 | 310 | 0 | 312 | 0 | 67 | 140 | 10 | 0 | 80 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 103 | 0 | 0 | 3 | 8302.5 | 903 | 382 | 0 | 35 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1133 | 0 | 1458.47 | 0 | 48 | 0 | 35 | 111 | 0 | 88 | 28 | 8 | 0 | 0 | 25 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 51 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 170 | 110 | 220 | 0 | 422 | 1100 | 10 | 7208.47 | 15510.97
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 35 | 134 | 122 | 293 | 55 | 35 | 126 | 0 | 280 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 310 | 116 | 20 | 105 | 0 | 0 | 64 | 60 | 35 | 37 | 38 | 0 | 220 | 0 | 17 | 650 | 108 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 123 | 0 | 395 | 348 | 0 | 39 | 0 | 34 | 90 | 100 | 199 | 0 | 17 | 52 | 76 | 43 | 0 | 42 | 305 | 0 | 312 | 0 | 67 | 140 | 10 | 0 | 81 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 102 | 0 | 0 | 4 | 8243 | 903 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1136 | 0 | 1458.08 | 0 | 48 | 0 | 35 | 111 | 0 | 88 | 26 | 8 | 0 | 0 | 25 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 51 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 170 | 110 | 220 | 0 | 424 | 1088 | 10 | 7093.08 | 15336.08 | 104.27
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 35 | 134 | 122 | 293 | 55 | 35 | 126 | 0 | 280 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 125 | 20 | 22 | 0 | 310 | 115 | 25 | 103 | 0 | 0 | 64 | 60 | 35 | 37 | 38 | 0 | 220 | 0 | 27 | 650 | 90 | 0 | 0 | 15 | 0 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 0 | 395 | 350 | 0 | 40 | 0 | 34 | 90 | 100 | 199 | 0 | 17 | 43 | 78 | 43 | 0 | 41 | 310 | 0 | 312 | 0 | 67 | 141 | 10 | 0 | 81 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 104 | 0 | 0 | 6 | 8247 | 903 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1142 | 0 | 1459.54 | 0 | 48 | 0 | 35 | 113 | 0 | 88 | 26 | 8 | 0 | 0 | 25 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 52 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 423 | 1092 | 10 | 7057.54 | 15304.54 | 104.26
22:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 35 | 133 | 91 | 293 | 55 | 35 | 108 | 0 | 280 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 125 | 14 | 22 | 0 | 310 | 92 | 24 | 103 | 0 | 0 | 64 | 60 | 35 | 37 | 38 | 0 | 220 | 0 | 27 | 650 | 17 | 0 | 0 | 25.5 | 0 | 224 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 0 | 395 | 352 | 0 | 42 | 0 | 34 | 81 | 102 | 200 | 0 | 17 | 45 | 78 | 43 | 0 | 35 | 310 | 0 | 312 | 0 | 67 | 143 | 10 | 0 | 81 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 100 | 0 | 0 | 6 | 8093.5 | 903 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1148 | 0 | 1464.08 | 0 | 48 | 0 | 35 | 113 | 0 | 88 | 26 | 8 | 0 | 0 | 25 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 95 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 220 | 0 | 423 | 1090 | 10 | 6947.08 | 15040.58 | 104.25
23:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 18 | 35 | 133 | 45 | 293 | 55 | 32 | 72 | 0 | 280 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 35 | 20 | 22 | 0 | 325 | 95 | 16 | 97 | 0 | 0 | 64 | 60 | 35 | 37 | 12 | 0 | 220 | 0 | 30 | 650 | 17 | 0 | 0 | 25.5 | 0 | 223 | 0 | 0 | 0 | 1224 | 0 | 51 | 120 | 0 | 398 | 348 | 0 | 45 | 0 | 31 | 47 | 103 | 199 | 0 | 17 | 48 | 82 | 43 | 0 | 35 | 315 | 0 | 312 | 0 | 67 | 146 | 10 | 0 | 81 | 30 | 0 | 17 | 162 | 17 | 48 | 48 | 104 | 0 | 0 | 6 | 7847.5 | 903 | 384 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 1470.76 | 0 | 48 | 0 | 35 | 113 | 0 | 88 | 26 | 8 | 0 | 0 | 25 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 95 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 110 | 190 | 0 | 422 | 1096 | 10 | 7043.76 | 14891.26 | 104.24
Total KWH | 0 | 1559040 | 472800 | 0 | 0 | 0 | 0 | 0 | 8550000 | 0 | 0 | 520200 | 501840 | 2769552 | 1343040 | 4722611 | 1092606 | 531133 | 1582560 | 0 | 7251500 | 0 | 0 | 0 | 138603 | 6490185 | 0 | 0 | 184489 | 1419600 | 405000 | 523440 | 0 | 7648636.36 | 720109 | 180655 | 1415040 | 1600000 | 7200 | 562324 | 466800 | 235762 | 580800 | 419520 | 20879 | 5266865 | 0 | 467040 | 15614545.46 | 720945 | 0 | 0 | 298339.2 | 0 | 3183329 | 0 | 0 | 0 | 27638179 | 130140 | 1226472 | 1973818 | 1622545 | 9472000 | 8635600 | 0 | 1014240 | 0 | 698832 | 1112640 | 2411226 | 3437760 | 0 | 386250 | 1114920 | 1765440 | 632208 | 472755 | 570320 | 7605000 | 0 | 7879000 | 0 | 1549080 | 3637555 | 210120 | 0 | 1909440 | 709920 | 0 | 398000 | 3362380 | 427320 | 1147200 | 1152000 | 2626560 | 11550 | 264220 | 98880 | 176770558.02 | 21896000 | 9535968 | 0 | 68160 | 76032 | 912000 | 0 | 0 | 0 | 0 | 0 | 510480 | 26145450 | 0 | 30397455 | 0 | 320185 | 0 | 238656 | 769536 | 0 | 622800 | 135770 | 128818 | 341180 | 582940 | 181429 | 0 | 334496 | 4144182 | 0 | 0 | 0 | 0 | 0 | 8969163 | 0 | 28500 | 0 | 1043782 | 1054431 | 173367 | 1156070 | 0 | 0 | 0 | 32941.92 | 947520 | 3783 | 177024 | 4123000 | 2641000 | 5332080 | 0 | 8515512 | 26161454.55 | 100800 | 157801965.47 | 334572523.49

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-10-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13844.13 | MW | 12:00 Hr. | Energy Generated |  |  | 334.5725 |  | MKWHr.
| Day Peak Demand |  |  | 13844.13 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.569 |  | MKWHr.
| Evening Peak Generation |  |  | 15644.99 | MW | 19:00 Hr. | Energy Demand |  |  | 336.1415 |  | MKWHr.
| Evening Peak Demand |  |  | 15730.68 | MW | 19:00 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 12169 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 883.66 |  | MMCFD
| Maximum Generation of the Day |  |  | 15644.99 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.6495 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.8688 | 0 | 16.6536 | 0 | 0 | 0.18449 | 0 | 0 | 47.7068 | Gas | 122.0957 | Gas | 438422658.1012
| Chattogram Zone |  |  | 5.2504 | 43.2527 | 5.6003 | 0 | 5.2669 | 0.15102 | 0 | 0.0072 | 59.5285 | Coal | 109.2419 | Coal | 693288313.7172
| Cumilla Zone |  |  | 25.4672 | 0 | 8.8417 | 0 | 0 | 0.47275 | 1.7654 | 0 | 36.547 | HFO | 38.9507 | HFO | 698934504.448
| Mymensingh Zone |  |  | 2.6266 | 0 | 2.8254 | 0 | 0 | 0.27577 | 0 | 0 | 5.7277 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2605 | Hydro | 5.2669 | Hydro | 526686.5
| Khulna Zone |  |  | 9.536 | 26.1455 | 0.14419 | 0 | 0 | 0.51048 | 22.808 | 0 | 59.1441 | Solar | 4.0392 | Solar | 64040690.2272
| Barishal Zone |  |  | 7.9731 | 38.8 | 0.27782 | 0 | 0 | 0.003783 | 0 | 0 | 47.0547 | Import | 54.9709 | Import | 329419032.4
| Rajshahi Zone |  |  | 13.1133 | 0 | 2.3972 | 0 | 0 | 1.2871 | 30.3975 | 0 | 47.1951 | Wind | 0.0072 | Wind | 105912
| Rangpur Zone |  |  | 0 | 1.0438 | 2.2105 | 0 | 0 | 1.1538 | 0 | 0 | 4.4081
| Total |  |  | 122.0957 | 109.2419 | 38.9507 | 0 | 5.2669 | 4.0392 | 54.9709 | 0.0072 | 334.5725
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 438422658.1012 |  | Hydro | 526686.5
|  |  |  | Coal | 693288313.7172 |  | Solar | 64040690.2272
|  |  |  | HFO | 698934504.448 |  | Import | 329419032.4
|  |  |  | HSD | 0 |  | Wind | 105912
[5 empty] | Total: | 222,47,37,797 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.896 | Peak Hr Flow | 903.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51286818.25 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.3975 | Peak Hr Flow | 1461.29 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2430 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.7654 | Peak Hr Flow | 88.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2686 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.0589 | Peak Hr Flow | 2452.29 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 12 |  | 5577
|  |  |  | Chattogram |  | 0 |  | 1571
|  |  |  | Cumilla |  | 0 |  | 1477
|  |  |  | Mymensingh |  | 70 |  | 1168
|  |  |  | Sylhet |  | 0 |  | 645
|  |  |  | Khulna |  | 0 |  | 1789
|  |  |  | Barishal |  | 0 |  | 474
|  |  |  | Rajshahi |  | 0 |  | 1396
|  |  |  | Rangpur |  | 0 |  | 881
|  |  |  | Total |  | 82 |  | 14978
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:03 |  | Shyampur-Shyampur(New) 132kV Ckt-2 Scheduled S/D from Shyampur 230/132kV end Due to
Overhead Transmission Line Reconducting.
| 08:06 |  | Bagabari-Bera 132 KV ckt S/D. (Bera PS disconnected from Bagabari side).
|  | 08:16 | Barishal 132/33kV S/S T-2 (415T) HT is restored.
|  | 08:17 | Barishal 132/33kV S/S T-2 (415T) LT is restored.
| 08:31 | 15:12 | Ishwardi-Rooppur 132kV Ckt-1 Scheduled S/D from Ruppur 132/11kV end Due to Annual
Maintenance and from Ishurdi 132/33kV end Due to Annual maintenance
| 08:34 | 14:35 | Noapara 132/33kV S/S T-2 LT Scheduled S/D
| 08:34 | 14:34 | Noapara 132/33kV S/S T-2 HT Scheduled S/D
| 08:53 | 09:30 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Scheduled S/D | [7 empty] | 30.0MW load
interrup.
| 08:53 | 09:30 | Bhaluka 132/33kV S/S 02. Transformer- 02 HT Scheduled S/D | [7 empty] | 30.0MW load
interrup.
| 09:02 | 19:45 | Gopalganj 400/132kV S/S 400kV Rooppur Project Work S/D
| 09:09 |  | Goalpara 132/33kV S/S T-6 LT Forced S/D Due to Bad Noise Heard in 33 kV side PT(R-Phase)
| 09:10 |  | Goalpara 132/33kV S/S T-6 HT Forced S/D Due to Bad Noise Heard in 33 kV side PT(R-Phase)
| 09:22 | 13:53 | Agrabad-Rampur 132kV Ckt-1 Scheduled S/D from Agrabad 132/33kV end Due to SF6 Gas
Analyzing Test
| 09:23 | 17:26 | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T LT Scheduled S/D Due to Annual
maintenance work
| 09:24 | 17:25 | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T HT Scheduled S/D Due to Annual
maintenance work
| 09:25 | 13:52 | Rampur 230/132/33 S/S Agrabad-1 Scheduled S/D
|  | 09:25 | Madaripur 132/33kV S/S T1-405T HT is restored.
| 09:31 | 17:10 | Bashundhara-Tongi 132 kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
maintenance work (dead line checking)
|  | 09:32 | Madaripur 132/33kV S/S T1-405T LT is restored.
|  | 09:34 | Haripur-Meghnaghat 230kV Ckt-2 is restored.
| 09:40 | 14:49 | Muktagacha 132/33kV S/S RPCL-2 Scheduled S/D Due to Annual maintenance.
| 09:41 | 16:55 | Aminbazar 400/230/132kV S/S 132 kv Bus 02 Scheduled S/D Due to Anual Maintenance
| 09:41 | 17:22 | Meghnaghat 400/230kV S/S 400 kV Bus -01 Project Work S/D Due to Shutdown for project work
| 09:51 |  | Sikalbaha 225 MW CCPP ST was sync.
| 09:52 | 17:23 | Aminbazar-Meghnaghat 400kV Ckt-2 Project Work S/D from Meghnaghat 400/230kV end Due to
Shutdown for project work and from Aminbazar 400/230/132kV end Due to Work in Meghnaghat
end
| 09:55 | 17:15 | Aminbazar-Meghnaghat 400kV Ckt-2 Forced S/D from Aminbazar 400/230/132kV end Due to Work
in Meghnaghat end
| 09:59 | 16:59 | Barapukuria 230/132/33kV S/S 132 KV Bus B Scheduled S/D Due to Annual maintenance work
| 10:08 | 16:53 | Madaripur 132/33kV S/S T2-415T LT Scheduled S/D Due to Annual Maintenance Work
| 10:08 | 16:53 | Madaripur 132/33kV S/S T2-415T HT Scheduled S/D Due to Annual Maintenance Work.
|  | 11:06 | Haripur 230/132kV S/S 132KV Bhulta-1 (Old Narsingdi) is restored.
| 11:27 | 14:54 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Project Work S/D Due to
Painting & 33 Kv Bushing Maintanence
| 11:28 | 14:54 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Project Work S/D Due to
Painting & 33 Kv Bushing Maintanence
| 12:00 |  | Day Peak Generation: 13840 MW.
| 12:20 | 12:43 | Shahjibazar 132/33kV S/S TR-04 HT Tripped showing Lockout Relay relays Due to Flashing in
33kv switchyard bus
| 12:20 | 13:16 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing O/C,E/F relays Due to Flashing in 33kv
switchyard bus
| 12:20 | 13:14 | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing Lockout Relay relays Due to Flashing in
33kv switchyard bus
| 12:20 | 12:47 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing Lockout Relay relays Due to Flashing in
33kv switchyard bus
| 12:53 |  | Raozan unit-2 was shutdown due to gas shortage.
| 12:57 | 14:04 | Haripur 230/132kV S/S Bus-2 Scheduled S/D Due to 230 KV Meghnaghat-2 and 210 MW
Siddhirganj PS Bay Isolator finger changing work.
| 13:24 | 16:42 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 LT Scheduled S/D Due to Red Hot Maintenance
Work
| 13:24 | 16:42 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 HT Scheduled S/D Due to Red Hot Maintenance
Work
| 13:53 |  | Bheramara 410 MW CCPP, FGMO is OFF with remarks:-
|  | 15:52 | Chauddagram-Cumilla(S) 132 kV Ckt-1 is restored.
|  | 16:25 | Patuakhali 132/33kV S/S 415T (T-2) HT is restored.
|  | 16:26 | Patuakhali 132/33kV S/S 415T (T-2) LT is restored.
|  | 16:51 | Lalmonirhat 132/33kV S/S T-1 (425T) LT is restored.
|  | 16:51 | Lalmonirhat 132/33kV S/S T-1 (425T) HT is restored.
|  | 17:45 | Gopalganj 400/132kV S/S ATR-04 HT is restored.
|  | 17:45 | Gopalganj 400/132kV S/S ATR-04 LT is restored.
| 19:00 |  | Evening Peak Generation is 15644 MW.
| 20:17 | 22:35 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to Red hot maintenance | [7 empty] | 15.0MW load
interrup.
| 20:18 | 22:34 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to Red hot maintenance | [7 empty] | 15.0MW load
interrup.
| 21:36 | 22:34 | Barapukuria-Saidpur 132 kV Ckt-1 Tripped from Barapukuria 230/132/33kV end showing REL
511,94HR, 94HY,94HB relays Due to Saidpur end 132KV Lightning Arrester blast of B-phase
| 21:36 | 22:33 | Barapukuria-Rangpur 132 kV Ckt-2 Tripped from Saidpur 132/33kV end showing Distance Relay
Optd. relays Due to Lighting Arrestor ( B phase) Burst
| 06:00 |  | Minimum gen. is 12334 MW.
| 07:07 |  | Barapukuria - Purbasadipur 230KV CKT-1&2 S/D
| 07:08 |  | Gopalganj 400/132kV S/S 230kV Barisal CKT-01 Project Work S/D
| 07:08 |  | Patuakhali 132/33kV S/S 415T (T-2) LT Scheduled S/D Due to Annual Maintenance-2025
| 07:09 |  | Patuakhali 132/33kV S/S 415T (T-2) HT Scheduled S/D Due to Annual Maintenance-2025
| 07:09 |  | Barishal 230/132kV S/S Gopalgonj CKT-1 Project Work S/D Due to Barishal North to
Patuakhali ckt stringing work
| 07:14 |  | At Bhola GT,(120/140)MVA Transformer is S/D. Taken by Borhanuddin PBS due red hot
maintenance at CT clamp.Interruption 70 MW.
| 07:24 |  | Chauddagram-Cumilla(S) 132 kV Ckt-2 Scheduled S/D from Cumilla(S) 132/33kV end Due to
Annual Maintenance
| 07:29 |  | Madaripur 132/33kV S/S T2-415T LT Scheduled S/D Due to Annual Maintenance work
| 07:30 |  | Madaripur 132/33kV S/S T2-415T HT Scheduled S/D Due to Annual Maintenance Work
| 07:37 |  | Kalurghat 132/33kV S/S TRFO-02(516T) LT Forced S/D Due to পাওয়ার ট্রান্সফরমার -২ এর LT
সাইডে Bus side- DS & 33 KV cable connector high ট্যাম্প: জনিত মেরামত কাজের জন্য।
| 07:40 |  | Madaripur 132/33kV S/S 33 KV BUS Scheduled S/D Due to Madaripur pbs maintenance work. | [7 empty] | 16.0MW load
interrup.
| 07:43 |  | Sholosohor 132/33kV S/S TRAFO-01 LT Scheduled S/D Due to Annual Maintenance
| 07:43 |  | Sholosohor 132/33kV S/S TRAFO-01 HT Scheduled S/D Due to Annual Maintenance
| 07:49 |  | Gopalganj 400/132kV S/S 400kV Bus-01 Scheduled S/D Due to Annual maintenance
| 07:59 |  | Barapukuria-Bogura 230 kV Ckt-2 Project Work S/D from Barapukuria 230/132/33kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-10-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | -
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 350 | 8550000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 7251500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1092606 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 208.137 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6490185 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 520200 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 122 | 1343040 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 531133 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 138603 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 405000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 523440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 472800 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 293 | 4722611 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 134 | 2769552 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1559040 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1582560 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 184489 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 501840 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 310 | 7648636.36 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1419600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6655.861 | 2358 | 47706835.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 1600000 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 298339.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 130140 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | “Fuel transfer halted: terminal–plant road work.”
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5266865 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 3183329 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 50 | 466800 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 64 | 562324 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 580800 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 467040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 1415040 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20879 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 20 | 180655 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 235762 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 419520 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 112 | 720109 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 159.86 | 160 | 720945 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 27638179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 7200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 650 | 15614545.46 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.723 | 2957.5 | 59528471.66
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 0 | 0 | Shutdown for Major Overhaul
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 346 | 8635600 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 410 | 9472000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 30 | 698832 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 41 | 1014240 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 1622545 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1226472 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 117 | 1973818 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 570320 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2411226 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 199 | 3437760 | -
| Import (Tripura) |  | Import | 0 | 160 | 88 | 1765440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 632208 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 386250 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1114920 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 84 | 1112640 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 472755 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1661 | 36547026
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 102 | 2626560 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 1152000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 48 | 1147200 | Avil100%;NEO cut for BPDB late pay PPA Sec.13.2(j)
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 264220 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 3 | 98880 | To be dispatched 06 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 427320 | Liquid fuel shortage due to fund crisis
Mymensingh Area Total |  |  |  |  | 654.21 | 218 | 5727730
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1549080 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 143 | 3637555 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 709920 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1909440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 162 | 3362380 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 398000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 10 | 210120 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7605000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 312 | 7879000 | load is partial due to one IDCT shut down
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1131 | 27260495
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 903 | 21896000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 41 | 68160 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 40 | 76032 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 382 | 9535968 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 510480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1148.28 | 1182 | 26145450 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3653.28 | 2586 | 59144090
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 622 | 424 | 8515512 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 59 | 177024 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2641000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 26161454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5332080 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 10 | 100800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 170 | 4123000 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3783 | -
Barishal Area Total |  |  |  |  | 2858 | 2113 | 47054653.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 341180 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 320185 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 135770 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 173 | 4144182 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 348 | 8969163 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 181429 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 128818 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 622800 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 108 | 769536 | Fuel shortage as BPDB payment not done in time
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 238656 | Fuel shortage as BPDB payment not done in time
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28500 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1461.29 | 30397455 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 334496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 582940 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3518.96 | 2368.49 | 47195110
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 51 | 1043782 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1156070 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32941.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1054431 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 173367 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 947520 | -
Rangpur Area Total |  |  |  |  | 950 | 252 | 4408111.92
Eastern Grid Total |  |  |  |  | 17383.855 | 8325.5 | 176770558.02
Western Grid Total |  |  |  |  | 10980.24 | 7319.49 | 157801965.47
National Grid Total |  |  |  |  | 28364.095 | 15644.99 | 334572523.49
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-10-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10355.59 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4539.6 | MW
i) Dhaka area |  |  | 5564.54 |  | MW | i) Khulna area |  |  |  | 1789 | MW
ii) Chattogram area |  |  | 1570.9 |  | MW | ii) Barishal area |  |  |  | 474 | MW
iii) Cumilla area |  |  | 1477.15 |  | MW | iii) Rajshahi area |  |  |  | 1395.6 | MW
iv) Mymensingh area |  |  | 1098 |  | MW | iv) Rangpur area |  |  |  | 881 | MW
v) Sylhet area |  |  | 645 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14895.19 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 88 | 18:00 | 133 | Niamatpur | 75 | 18:00
2 | AKSML | 149.6 | 00:00 | 68 | Ishurdi | 76 | 18:00 | 134 | Noapara | 46 | 18:30
3 | Aftabnagar | 40 | 18:00 | 69 | Jaldhaka | 72 | 18:30 | 135 | PHP | 6 | 00:00
4 | Agargaon | 135 | 13:00 | 70 | Jamalpur | 110 | 13:00 | 136 | Pabna | 102 | 18:00
5 | Agrabad | 104 | 13:00 | 71 | Jashore | 144 | 18:30 | 137 | Palashbari | 116 | 18:00
6 | Amnura | 33 | 18:00 | 72 | Jhenaidah | 127 | 19:00 | 138 | Panchagarh | 57 | 18:00
7 | Ashuganj | 91 | 01:00 | 73 | Joydebpur | 158 | 18:00 | 139 | Patiya | 10 | 00:00
8 | BSRM | 206 | 06:00 | 74 | Joypurhat | 57 | 00:00 | 140 | Patuakhali | 71 | 22:00
9 | Bagerhat | 83 | 19:30 | 75 | Juldah | 16.5 | 13:00 | 141 | Payra | 32 | 00:00
10 | Bajitpur | 78 | 20:00 | 76 | KSRM | 42 | 08:00 | 142 | Postogola | 70 | 01:00
11 | Bakulia | 88 | 18:30 | 77 | Kabirpur | 248 | 18:30 | 143 | Purbachal | 23 | 19:30
12 | Banani | 55 | 13:00 | 78 | Kachua | 94 | 20:00 | 144 | Purbasadipur | 114 | 18:30
13 | Bangabhaban | 27 | 10:00 | 79 | Kallyanpur | 108 | 23:00 | 145 | Rahanpur | 33 | 20:00
14 | Barapukuria | 61 | 18:00 | 80 | Kalurghat | 54 | 11:00 | 146 | Rahim | 37 | 09:00
15 | Barguna | 22 | 22:00 | 81 | Kamrangirchar | 82 | 16:00 | 147 | Rajbari | 81 | 18:00
16 | Barishal | 116 | 18:00 | 82 | Kaptai | N/A | N/A | 148 | Rajendrapur | 130 | 19:00
17 | Barishal-230 | 100 | 18:30 | 83 | Kasba | 36 | 19:30 | 149 | Rajshahi | 105 | 18:00
18 | Baroaulia | 75 | 18:30 | 84 | Kazla | 100 | 19:00 | 150 | Rajshahi-230 | 90 | 13:00
19 | Baroirhat | 67 | 20:00 | 85 | Keranigonj | 82 | 00:00 | 151 | Ramganj | 122 | 19:30
20 | Bashundhara | 223 | 15:00 | 86 | Khagrachori | 36 | 18:00 | 152 | Rampur | 44 | 00:00
21 | BashundharaCement | 8 | 00:00 | 87 | Khulna | 78 | 13:00 | 153 | Rangamati | 18 | 18:00
22 | Beanibazar | 78 | 18:00 | 88 | Khulshi | 186 | 18:30 | 154 | Rangpur | 137 | 18:30
23 | Benapole | 62 | 19:30 | 89 | Kishoreganj | 130 | 21:00 | 155 | Ruppur | 8.4 | 11:00
24 | Bhaluka | 148 | 19:30 | 90 | Kodda | 306 | 18:30 | 156 | SSM | 5 | 23:00
25 | Bhandaria | 54 | 18:00 | 91 | Kulaura | 55 | 18:00 | 157 | Saidpur | 99 | 18:00
26 | Bhangura | 37 | 18:00 | 92 | Kurigram | 63 | 18:00 | 158 | Satkhira | 125 | 19:00
27 | Bheramara(GK) | 66 | 18:00 | 93 | Kushtia | 151 | 18:00 | 159 | Satmasjid | 107 | 18:00
28 | Bhulta | 225 | 12:00 | 94 | Laksam | 34 | 21:00 | 160 | Savar | 224 | 18:30
29 | Bog-Sherpur | 62 | 18:30 | 95 | Lakshmipur | 34 | 21:00 | 161 | SevenRings | 18.76 | 03:00
30 | Bogura | 164 | 20:00 | 96 | Lalbag | 60 | 13:00 | 162 | ShahCement | 15 | 00:00
31 | Borhanuddin | 94 | 21:00 | 97 | Lalmonirhat | 56 | 18:00 | 163 | Shahjadpur | 90 | 18:00
32 | Brahmanbaria | 132 | 20:00 | 98 | MI_Cement | 16 | 02:00 | 164 | Shahjibazar | 128 | 18:00
33 | Cantonment | 152 | 13:00 | 99 | Madanganj | 48 | 13:00 | 165 | Shahmirpur | 63 | 18:00
34 | Chandina | 18.96 | 17:00 | 100 | Madaripur | 114 | 22:00 | 166 | Shariatpur | 89 | 21:00
35 | Chandpur | 84 | 20:00 | 101 | Madartek | 101 | 23:00 | 167 | Sherpur | 114 | 00:00
36 | Chandraghona | 35 | 18:00 | 102 | Madunaghat | 62 | 18:00 | 168 | Shikalbaha | 29 | 17:00
37 | Chapai | 69 | 19:30 | 103 | Magura | 66 | 18:00 | 169 | Shitalakhya | 86.9 | 16:00
38 | Charsaidpur | 33 | 07:00 | 104 | Mahasthangarh | 70 | 00:00 | 170 | Sholosohor | 49 | 16:00
39 | Chauddagram | 72 | 20:00 | 105 | Maijdee | 40 | 21:00 | 171 | Shyampur | 124 | 01:00
40 | Chhatak | 36 | 18:30 | 106 | Manikganj | 129 | 19:30 | 172 | Siddhirganj | 129 | 16:00
41 | Chowmuhani | 173 | 18:30 | 107 | Maniknagar | 64 | 13:00 | 173 | Sirajganj | 116 | 19:00
42 | Chuadanga | 115 | 18:30 | 108 | Matarbari | 53 | 18:00 | 174 | Sonargaon | 144 | 18:30
43 | Coxsbazar | 144 | 18:00 | 109 | Matuail | 70 | 11:00 | 175 | Sreemongol | 86 | 19:00
44 | Cumilla(N) | 144 | 19:30 | 110 | Metrorail_Motijheel | 30 | 18:00 | 176 | Sreepur | 114 | 18:00
45 | Cumilla(S) | 165 | 18:00 | 111 | Metrorail_Uttara | 8 | 13:00 | 177 | Srinagar | 49.4 | 21:00
46 | Daganbhuiyan | N/A | N/A | 112 | Millgate | 129 | 15:00 | 178 | Sunamganj | 60 | 21:00
47 | Daudkandi | 158 | 19:30 | 113 | Mirpur | 141 | 18:30 | 179 | Sylhet | 51 | 18:30
48 | DhakaUniversity | 74 | 13:00 | 114 | Mirsorai | 12 | 18:00 | 180 | Sylhet-132 | 128 | 18:00
49 | Dhamrai | 124 | 16:00 | 115 | Mirzapur | 47 | 19:30 | 181 | TK | 24 | 00:00
50 | Dhanmondi | 143.5 | 13:00 | 116 | Mithapukur | 56 | 18:00 | 182 | Tangail | 170 | 19:00
51 | Dohazari | 108 | 00:00 | 117 | Modern | N/A | N/A | 183 | Taraganj | 23 | 18:00
52 | Faridpur | 167 | 18:30 | 118 | Mogbazar | 107.2 | 13:00 | 184 | Thakurgaon | 97 | 18:30
53 | Fatullah | 115 | 11:00 | 119 | Mongla | 39 | 18:00 | 185 | Tongi | 155 | 18:00
54 | Fenchuganj | 42 | 18:00 | 120 | Motijheel | 77 | 13:00 | 186 | Ullahpara | 39 | 18:00
55 | Feni | 126 | 18:00 | 121 | Muktagacha | 34 | 18:30 | 187 | Ullon | 71 | 20:00
56 | GPH | 84 | 13:00 | 122 | Munshiganj | 108 | 20:00 | 188 | Uttara | 104 | 12:00
57 | Ghatail | 72 | 18:30 | 123 | Muradnagar | 41 | 20:00 | 189 | UttaraNew | 37 | 00:00
58 | Ghorashal | 0 | 00:00 | 124 | Mymensingh | 204 | 18:00 | 190 | Zigatola | 77 | 18:00
59 | Ghorashal-230 | 102 | 21:00 | 125 | Naogaon | 118 | 18:30
60 | Goalpara | 42 | 00:00 | 126 | Narail | 58 | 18:00
61 | Gollamari | 92 | 23:00 | 127 | Narinda | 74 | 13:00
62 | Gopalganj | 108 | 18:30 | 128 | Narshingdi | 173 | 23:00
63 | Gulshan | 136 | 12:00 | 129 | Natore | 146 | 18:00
64 | Halishahar | 75.5 | 16:00 | 130 | Nawabganj | 47.2 | 21:00
65 | HaripurSBU | 167 | 12:00 | 131 | Netrakona | 135 | 19:00
66 | Hasnabad | 110 | 19:00 | 132 | New | 58 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-10-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14536.5 | 90 |  | 14630.55
1:00 | 13973.5 | 64 |  | 14040.5
2:00 | 13505.5 | 62 |  | 13570.5
3:00 | 13134.5 | 63 |  | 13200.5
4:00 | 12682.5 | 55 |  | 12739.5
5:00 | 12426 | 43 |  | 12471
6:00 | 12169 | 0 |  | 12169
7:00 | 12244.92 | 47 |  | 12293.92
8:00 | 12551.55 | 96 |  | 12651.87
9:00 | 12631.56 | 117 |  | 12753.83
10:00 | 12813.01 | 0 |  | 12813.01
11:00 | 13325.14 | 0 |  | 13325.14
12:00 | 13844.13 | 0 |  | 13844.13
13:00 | 14114.74 | 47 |  | 14163.74
14:00 | 14016.02 | 84 |  | 14103.8
15:00 | 13978.49 | 139 |  | 14123.75
16:00 | 13814.24 | 133 |  | 13953.23
17:00 | 13702.26 | 105 |  | 13811.99
18:00 | 15321.65 | 123 |  | 15450.19
19:00 | 15644.99 | 82 |  | 15730.68
19:30 | 15510.97 | 76 |  | 15590.39
20:00 | 15336.08 | 61 |  | 15399.83
21:00 | 15304.54 | 49 |  | 15355.75
22:00 | 15040.58 | 33 |  | 15074.58
23:00 | 14891.26 | 76 |  | 14970.26
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-10-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7548.5 | 6988 | 14536.5 | DAILY GENERATION CURVE
00:30 | 7368.5 | 6886.5 | 14255
01:00 | 7188.5 | 6785 | 13973.5 | 27-10-2025
01:30 | 7014 | 6725.5 | 13739.5
02:00 | 6839.5 | 6666 | 13505.5
02:30 | 6712 | 6608 | 13320
03:00 | 6584.5 | 6550 | 13134.5
03:30 | 6455.5 | 6453 | 12908.5
04:00 | 6326.5 | 6356 | 12682.5
04:30 | 6293.25 | 6261 | 12554.25
05:00 | 6260 | 6166 | 12426
05:30 | 6225 | 6072.5 | 12297.5
06:00 | 6190 | 5979 | 12169
06:30 | 6368.375 | 5838.585 | 12206.96
07:00 | 6546.75 | 5698.17 | 12244.92
07:30 | 6656.34 | 5741.895 | 12398.235
08:00 | 6765.93 | 5785.62 | 12551.55
08:30 | 6727.98 | 5863.575 | 12591.555
09:00 | 6690.03 | 5941.53 | 12631.56
09:30 | 6751.54 | 5970.745 | 12722.285
10:00 | 6813.05 | 5999.96 | 12813.01
10:30 | 6970.195 | 6098.88 | 13069.075
11:00 | 7127.34 | 6197.8 | 13325.14
11:30 | 7311.7 | 6272.935 | 13584.635
12:00 | 7496.06 | 6348.07 | 13844.13
12:30 | 7505.23 | 6474.205 | 13979.435
13:00 | 7514.4 | 6600.34 | 14114.74
13:30 | 7438.415 | 6626.965 | 14065.38
14:00 | 7362.43 | 6653.59 | 14016.02
14:30 | 7371.68 | 6625.575 | 13997.255
15:00 | 7380.93 | 6597.56 | 13978.49
15:30 | 7355.06 | 6541.305 | 13896.365
16:00 | 7329.19 | 6485.05 | 13814.24
16:30 | 7339.085 | 6419.165 | 13758.25
17:00 | 7348.98 | 6353.28 | 13702.26
17:30 | 7755.49 | 6756.465 | 14511.955
18:00 | 8162 | 7159.65 | 15321.65
18:30 | 8243.75 | 7239.57 | 15483.32
19:00 | 8325.5 | 7319.49 | 15644.99
19:30 | 8302.5 | 7208.47 | 15510.97
20:00 | 8243 | 7093.08 | 15336.08
20:30 | 8245 | 7075.31 | 15320.31 |  | Executive Engineer
21:00 | 8247 | 7057.54 | 15304.54 |  | Network Operation Division
21:30 | 8170.25 | 7002.31 | 15172.56
22:00 | 8093.5 | 6947.08 | 15040.58
22:30 | 7970.5 | 6995.42 | 14965.92
23:00 | 7847.5 | 7043.76 | 14891.26

## En-Curve
QF-LDC-12
Date | 27-10-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3519 | 1681 | 904 | 38 | 80 | 1463 | 218 | 4783 | 0 | 428 | 1422.5 | 0 | 0 | 0 | 90 | DAILY ENERGY CURVE
00:30 | 3468.5 | 1674.5 | 904.5 | 38 | 77 | 1461.5 | 218.5 | 4762 | 0 | 321 | 1329.5 | 0 | 0 | 0 | 77 | 27-10-2025
01:00 | 3418 | 1668 | 905 | 38 | 74 | 1460 | 219 | 4741 | 0 | 214 | 1236.5 | 0 | 0 | 0 | 64
01:30 | 3390 | 1670.5 | 904.5 | 38 | 73 | 1462.5 | 219.5 | 4701 | 0 | 214 | 1066.5 | 0 | 0 | 0 | 63 | Energy Generated | 334.5725 |  | MKWHr
02:00 | 3362 | 1673 | 904 | 38 | 72 | 1465 | 220 | 4661 | 0 | 214 | 896.5 | 0 | 0 | 0 | 62 | Energy not Served | 1.569 |  | MKWHr
02:30 | 3363.5 | 1673.5 | 904 | 38 | 71 | 1465 | 220 | 4671 | 0 | 160.5 | 753.5 | 0 | 0 | 0 | 62.5 | Total Energy Requirement | 336.1415 |  | MKWHr
03:00 | 3365 | 1674 | 904 | 38 | 70 | 1465 | 220 | 4681 | 0 | 107 | 610.5 | 0 | 0 | 0 | 63
03:30 | 3375.5 | 1661.5 | 904 | 38 | 73 | 1418.5 | 219.5 | 4623 | 0 | 107 | 488.5 | 0 | 0 | 0 | 59
04:00 | 3386 | 1649 | 904 | 38 | 76 | 1372 | 219 | 4565 | 0 | 107 | 366.5 | 0 | 0 | 0 | 55
04:30 | 3379.5 | 1656.75 | 904 | 38 | 72 | 1324.5 | 217.5 | 4539 | 0 | 107 | 316 | 0 | 0 | 0 | 49
05:00 | 3373 | 1664.5 | 904 | 38 | 68 | 1277 | 216 | 4513 | 0 | 107 | 265.5 | 0 | 0 | 0 | 43
05:30 | 3349.5 | 1663.5 | 904 | 38 | 66 | 1232.5 | 217 | 4461.5 | 0 | 107 | 258.5 | 0 | 0 | 0 | 21.5
06:00 | 3326 | 1662.5 | 904 | 38 | 64 | 1188 | 218 | 4410 | 0 | 107 | 251.5 | 0 | 0 | 0 | 0
06:30 | 3403.5 | 1672 | 904 | 38 | 60 | 1082.5 | 218 | 4352 | 36.71 | 109 | 331.25 | 0 | 0 | 0 | 23.5
07:00 | 3481 | 1681.5 | 904 | 38 | 56 | 977 | 218 | 4294 | 73.42 | 111 | 411 | 0 | 0 | 0 | 47
07:30 | 3470.5 | 1655.5 | 904.5 | 38 | 57 | 978.5 | 217.5 | 4286 | 154.235 | 130 | 506.5 | 0 | 0 | 0 | 71.5
08:00 | 3460 | 1629.5 | 905 | 38 | 58 | 980 | 217 | 4278 | 235.05 | 149 | 602 | 0 | 0 | 0 | 96
08:30 | 3409 | 1594.9 | 905 | 38 | 58 | 972.5 | 218.5 | 4256.5 | 340.655 | 163 | 635.5 | 0 | 0 | 0 | 106.5
09:00 | 3358 | 1560.3 | 905 | 38 | 58 | 965 | 220 | 4235 | 446.26 | 177 | 669 | 0 | 0 | 0 | 117
09:30 | 3369 | 1588.8 | 905 | 38 | 59 | 962.5 | 220.5 | 4135.5 | 515.985 | 186 | 742 | 0 | 0 | 0 | 58.5
10:00 | 3380 | 1617.3 | 905 | 38 | 60 | 960 | 221 | 4036 | 585.71 | 195 | 815 | 0 | 0 | 0 | 0
10:30 | 3371 | 1623.65 | 904.5 | 38 | 66.5 | 963 | 221 | 4109.5 | 620.425 | 198.5 | 953 | 0 | 0 | 0 | 0
11:00 | 3362 | 1630 | 904 | 38 | 73 | 966 | 221 | 4183 | 655.14 | 202 | 1091 | 0 | 0 | 0 | 0
11:30 | 3363.5 | 1649.4 | 904.5 | 38 | 73.5 | 1019 | 221.5 | 4267.5 | 606.735 | 203 | 1238 | 0 | 0 | 0 | 0
12:00 | 3365 | 1668.8 | 905 | 38 | 74 | 1072 | 222 | 4352 | 558.33 | 204 | 1385 | 0 | 0 | 0 | 0
12:30 | 3365 | 1679.9 | 904.5 | 38 | 79 | 1115.5 | 222 | 4385 | 585.035 | 205.5 | 1399.5 | 0 | 0 | 0.5 | 23.5
13:00 | 3365 | 1691 | 904 | 38 | 84 | 1159 | 222 | 4418 | 611.74 | 207 | 1414 | 0 | 0 | 1 | 47
13:30 | 3391 | 1611.2 | 904 | 38 | 78 | 1194.505 | 222 | 4441.5 | 556.175 | 203.5 | 1424 | 0 | 0 | 1.5 | 65.5
14:00 | 3417 | 1531.4 | 904 | 38 | 72 | 1230.01 | 222 | 4465 | 500.61 | 200 | 1434 | 0 | 0 | 2 | 84
14:30 | 3426.5 | 1540.4 | 903.5 | 38 | 71 | 1287.215 | 222 | 4464 | 421.64 | 194.5 | 1427.5 | 0 | 0 | 1 | 111.5
15:00 | 3436 | 1549.4 | 903 | 38 | 70 | 1344.42 | 222 | 4463 | 342.67 | 189 | 1421 | 0 | 0 | 0 | 139
15:30 | 3440 | 1539.7 | 903 | 38 | 71 | 1339.7 | 221.5 | 4482.5 | 243.965 | 189 | 1428 | 0 | 0 | 0 | 136
16:00 | 3444 | 1530 | 903 | 38 | 72 | 1334.98 | 221 | 4502 | 145.26 | 189 | 1435 | 0 | 0 | 0 | 133
16:30 | 3446.5 | 1513.5 | 903 | 38 | 70 | 1322.615 | 221 | 4478.5 | 82.135 | 219 | 1464 | 0 | 0 | 0 | 119
17:00 | 3449 | 1497 | 903 | 38 | 68 | 1310.25 | 221 | 4455 | 19.01 | 249 | 1493 | 0 | 0 | 0 | 105
17:30 | 3430 | 1499 | 903 | 38 | 77 | 1364.35 | 220 | 4691.5 | 9.505 | 471.5 | 1808.1 | 0 | 0 | 0 | 114
18:00 | 3411 | 1501 | 903 | 38 | 86 | 1418.45 | 219 | 4928 | 0 | 694 | 2123.2 | 0 | 0 | 0 | 123
18:30 | 3410 | 1505 | 903 | 38 | 87 | 1439.87 | 219.5 | 4874.5 | 0 | 746 | 2260.45 | 0 | 0 | 0 | 102.5
19:00 | 3409 | 1509 | 903 | 38 | 88 | 1461.29 | 220 | 4821 | 0 | 798 | 2397.7 | 0 | 0 | 0 | 82
19:30 | 3389 | 1510 | 903 | 38 | 76 | 1458.47 | 220 | 4750 | 0 | 827 | 2339.5 | 0 | 0 | 0 | 76
20:00 | 3394 | 1512 | 903 | 38 | 76 | 1458.08 | 220 | 4743 | 0 | 747 | 2245 | 0 | 0 | 0 | 61
20:30 | 3395.5 | 1520.5 | 903 | 38 | 77 | 1458.81 | 220 | 4748 | 0 | 738 | 2221.5 | 0 | 0 | 0 | 55
21:00 | 3397 | 1529 | 903 | 38 | 78 | 1459.54 | 220 | 4753 | 0 | 729 | 2198 | 0 | 0 | 0 | 49
21:30 | 3402 | 1528 | 903 | 38 | 78 | 1461.81 | 220 | 4729 | 0 | 710.5 | 2102.25 | 0 | 0 | 0 | 41
22:00 | 3407 | 1527 | 903 | 38 | 78 | 1464.08 | 220 | 4705 | 0 | 692 | 2006.5 | 0 | 0 | 0 | 33
22:30 | 3425.5 | 1529.5 | 903 | 38 | 80 | 1467.42 | 220 | 4708.5 | 0 | 624 | 1970 | 0 | 0 | 0 | 54.5
23:00 | 3444 | 1532 | 903 | 38 | 82 | 1470.76 | 220 | 4712 | 0 | 556 | 1933.5 | 0 | 0 | 0 | 76
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-10-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 07:00 | 362 | 16:00 | Payra | 410 | 07:00 | 403 | 18:30
Ashuganj | 400 | 6:00 | 378 | 16:00 | Rahanpur | 406 | 09:00 | 392 | 18:30
Bhulta | 397 | 07:00 | 369 | 16:00 | Rampal | 402 | 06:00 | 387 | 18:00
Bibiana | 386 | 07:00 | 378 | 18:00
BIPTC | 402 | 04:00 | 393 | 18:00
Bogura | 393 | 09:00 | 376 | 18:30
Gopalganj | 394 | 07:00 | 380 | 18:00
Kaliakoir | 370 | 07:00 | 358 | 18:00
Madunaghat | 392 | 12:00 | 387 | 00:00
Meghnaghat | 382 | 07:00 | 368 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 07:00 | 215 | 16:00 | Kaliakoir | 230 | 07:00 | 218 | 16:00
AKSML | 231 | 19:00 | 224 | 04:00 | Keranigonj | 223 | 07:00 | 213 | 16:00
Aminbazar | 227 | 07:00 | 216 | 13:00 | Khulna(S) | 233 | 09:00 | 219 | 18:30
Ashuganj | 228 | 07:00 | 215 | 15:00 | Madunaghat | 232 | 21:00 | 227 | 04:00
Ashuganj-400 | 228 | 6:00 | 216 | 16:00 | Madunaghat-400 | 232 | 20:00 | 228 | 01:00
Baghabari | 233 | 06:00 | 225 | 14:00 | Maniknagar | 217 | 07:00 | 209 | 15:00
Barapukuria | 230 | 10:00 | 211 | 18:00 | Meghnaghat | 223 | 09:00 | 118 | 16:00
Barapukuria-230 | 230 | 10:00 | 216 | 7:00 | Meghnaghat-400 | 223 | 07:00 | 214 | 14:00
Barishal | 233 | 07:00 | 224 | 15:00 | Mirsorai | 229 | 18:00 | 219 | 02:00
Bheramara | 234 | 09:00 | 222 | 14:00 | Rajshahi | 231 | 06:00 | 220 | 15:00
Bhulta | 227 | 07:00 | 208 | 16:00 | Rampal | 231 | 06:00 | 218 | 18:00
Bibiana | 230 | 07:00 | 221 | 18:30 | Rampur | N/A | N/A | N/A | N/A
BIPTC | 238 | 09:00 | 223 | 14:00 | Rampura | 225 | 07:00 | 206 | 15:00
Bogura | 239 | 09:00 | 229 | 18:30 | Shikalbaha | 231 | 21:00 | 225 | 00:00
Bogura-400 | 238 | 09:00 | 229 | 18:30 | Shyampur | 222 | 07:00 | 212 | 16:00
Borhanuddin | 235 | 06:00 | 229 | 21:00 | Siddhirganj | 218 | 05:00 | 213 | 12:00
BSRM | 226 | 12:00 | 219 | 03:00 | Sirajgonj | 237 | 07:00 | 231 | 15:00
Cumilla(N) | 222 | 07:00 | 215 | 15:00 | Sreepur | 224 | 07:00 | 213 | 15:00
Faridpur | 230 | 07:00 | 220 | 13:00 | Tongi | 225 | 00:00 | 212 | 18:00
Fenchuganj | 229 | 07:00 | 223 | 18:30
Ghorashal | 230 | 02:00 | 220 | 15:00
Ghorashal-230 | 225 | 07:00 | 210 | 15:00
Gopalganj | 231 | 06:00 | 222 | 13:00
GPH | 229 | 20:00 | 223 | 03:00
Haripur | 218 | 07:00 | 211 | 16:00
Hasnabad | 224 | 07:00 | 213 | 12:00
Hathazari | 229 | 19:30 | 222 | 16:00
Ishurdi | 237 | 09:00 | 225 | 14:00
Jhenaidah | 233 | 09:00 | 218 | 18:30
Kachua | 229 | 12:00 | 214 | 04:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 07:00 | 126 | 16:00 | Lalmonirhat | 130 | 09:00 | 120 | 16:00
Agargaon | 133 | 07:00 | 124 | 16:00 | Madanganj | 130 | 00:00 | 127 | 17:00
Agrabad | 131 | 21:00 | 127 | 02:00 | Madaripur | 134 | 07:00 | 128 | 18:00
AKS | 129 | 05:00 | 126 | 15:00 | Madartek | 137 | 06:00 | 124 | 16:00
Aminbazar | 133 | 04:00 | 126 | 23:00 | Madunaghat | 134 | 18:30 | 131 | 02:00
Amnura | 137 | 09:00 | 127 | 14:00 | Magura | 135 | 06:00 | 123 | 18:30
Ashuganj | 137 | 09:00 | 131 | 18:00 | Mahasthangarh | 132 | 06:00 | 126 | 15:00
Bagerhat | 130 | 09:00 | 115 | 18:00 | Maijdee | 131 | 09:00 | 124 | 00:00
Bajitpur | 127 | 00:00 | 119 | 15:00 | Manikganj | 130 | 01:00 | 120 | 16:00
Bakulia | 132 | 19:00 | 129 | 04:00 | Maniknagar | 131 | 05:00 | 125 | 12:00
Banani | 138 | 07:00 | 125 | 15:00 | Matarbari | 126 | 04:00 | 107 | 18:00
Bangabhaban | 131 | 06:00 | 124 | 12:00 | Matuail | 128 | 07:00 | 122 | 16:00
Barapukuria | 137 | 09:00 | 124 | 14:00 | Metrorail_Motijheel | 131 | 05:00 | 125 | 12:00
Barguna | 135 | 08:00 | 131 | 00:00 | Metrorail_Uttara | 134 | 01:00 | 124 | 16:00
Barishal | 132 | 07:00 | 125 | 22:00 | Millgate | 135 | 07:00 | 125 | 16:00
Barishal-230 | 133 | 06:00 | 126 | 23:00 | Mirpur | 133 | 07:00 | 125 | 12:00
Baroaulia | 133 | 19:00 | 129 | 02:00 | Mirzapur | 129 | 10:00 | 118 | 06:00
Baroirhat | 130 | 08:00 | 125 | 04:00 | Mithapukur | 133 | 23:00 | 124 | 14:00
Bashundhara | 138 | 07:00 | 124 | 16:00 | MI_Cement | 128 | 07:00 | 123 | 12:00
BashundharaCement | 130 | 00:00 | 127 | 16:00 | Modern | N/A | N/A | N/A | N/A
Beanibazar | 129 | 07:00 | 123 | 18:00 | Mogbazar | 139 | 05:00 | 125 | 16:00
Benapole | 133 | 05:00 | 117 | 18:30 | Mongla | 130 | 09:00 | 118 | 18:00
Bhaluka | 125 | 07:00 | 118 | 14:00 | Motijheel | 131 | 05:00 | 124 | 12:00
Bhandaria | 129 | 08:00 | 119 | 23:00 | Muktagacha | 128 | 08:00 | 117 | 18:30
Bhangura | 133 | 06:00 | 127 | 16:00 | Munshiganj | 126 | 07:00 | 122 | 13:00
Bheramara | 138 | 09:00 | 133 | 14:00 | Muradnagar | 126 | 09:00 | 121 | 18:30
Bheramara(GK) | 138 | 05:00 | 133 | 16:00 | Mymensingh | 129 | 08:00 | 108 | 18:00
Bhulta | 126 | 07:00 | 120 | 16:00 | Naogaon | 129 | 06:00 | 124 | 01:00
Bog-Sherpur | 134 | 09:00 | 127 | 16:00 | Narail | 137 | 09:00 | 123 | 18:30
Bogura | 134 | 09:00 | 129 | 15:00 | Narinda | 131 | 5:00 | 125 | 12:00
Bogura-230 | 135 | 09:00 | 129 | 15:00 | Narshingdi | 130 | 09:00 | 118 | 00:00
Brahmanbaria | 130 | 02:00 | 122 | 18:00 | Natore | 134 | 05:00 | 128 | 15:00
Cantonment | 132 | 07:00 | 124 | 15:00 | Nawabganj | 132 | 07:00 | 125 | 12:00
Chandina | 130 | 07:00 | 125 | 15:00 | Netrakona | 120 | 03:00 | 108 | 18:00
Chandpur | 137 | 12:00 | 130 | 00:00 | New | 136 | 07:00 | 126 | 18:00
Chandraghona | 134 | 19:00 | 132 | 04:00 | Niamatpur | 138 | 06:00 | 133 | 00:00
Chapai | 138 | 09:00 | 133 | 00:00 | Noapara | 133 | 09:00 | 121 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 07:00 | 123 | 11:00 | Pabna | 136 | 07:00 | 129 | 16:00
Chauddagram | 130 | 07:00 | 125 | 00:00 | Palashbari | 128 | 09:00 | 121 | 18:00
Chhatak | 127 | 06:00 | 121 | 18:00 | Panchagarh | 139 | 09:00 | 125 | 12:00
Chowmuhani | 131 | 17:00 | 125 | 00:00 | Patiya | 131 | 21:00 | 126 | 03:00
Chuadanga | 134 | 09:00 | 119 | 18:00 | Patuakhali | 135 | 08:00 | 132 | 00:00
Coxsbazar | 117 | 08:00 | 108 | 18:00 | Payra | 136 | 08:00 | 133 | 18:00
Cumilla(N) | 129 | 07:00 | 125 | 00:00 | PHP | 130 | 08:00 | 126 | 00:00
Cumilla(S) | 130 | 07:00 | 126 | 00:00 | Postogola | 132 | 07:00 | 124 | 12:00
Daganbhuiyan | N/A | N/A | N/A | N/A | Purbachal | 138 | 07:00 | 125 | 15:00
Daudkandi | 123 | 09:00 | 117 | 23:00 | Purbasadipur | 133 | 20:00 | 120 | 14:00
DhakaUniversity | 139 | 07:00 | 125 | 15:00 | Rahanpur | 140 | 09:00 | 134 | 18:00
Dhamrai | 132 | 07:00 | 122 | 16:00 | Rahanpur-400 | 140 | 09:00 | 135 | 18:00
Dhanmondi | 138 | 05:00 | 126 | 15:00 | Rahim | 127 | 02:00 | 123 | 11:00
Dohazari | 126 | 07:00 | 123 | 00:00 | Rajbari | 135 | 06:00 | 127 | 18:30
Faridpur | 136 | 06:00 | 130 | 00:00 | Rajendrapur | 132 | 20:00 | 117 | 16:00
Fatullah | 135 | 07:00 | 124 | 11:00 | Rajshahi | 133 | 01:00 | 127 | 14:00
Fenchuganj | 135 | 07:00 | 131 | 18:00 | Rajshahi-230 | 132 | 06:00 | 127 | 13:00
Feni | 129 | 07:00 | 125 | 00:00 | Ramganj | 132 | 11:00 | 124 | 04:00
Ghatail | 126 | 05:00 | 117 | 18:30 | Rampur | 131 | 20:00 | 127 | 10:00
Ghorashal | 137 | 06:00 | 127 | 16:00 | Rampura | 138 | 07:00 | 126 | 15:00
Goalpara | 133 | 08:00 | 123 | 18:30 | Rangamati | 133 | 07:00 | 130 | 16:00
Gollamari | 134 | 08:00 | 123 | 18:00 | Rangpur | 133 | 23:00 | 123 | 16:00
Gopalganj | 133 | 06:00 | 125 | 18:00 | Ruppur | 139 | 09:00 | 132 | 16:00
Gopalganj-400 | 135 | 06:00 | 130 | 15:00 | Saidpur | 135 | 09:00 | 121 | 16:00
Gulshan | 138 | 07:00 | 126 | 15:00 | Satkhira | 131 | 09:00 | 117 | 18:00
Halishahar | 132 | 19:30 | 127 | 16:00 | Satmasjid | 132 | 06:00 | 124 | 16:00
Haripur | 128 | 07:00 | 123 | 12:00 | Savar | 132 | 07:00 | 125 | 14:00
HaripurSBU | 128 | 08:00 | 123 | 15:00 | SevenRings | 137 | 07:00 | 128 | 16:00
Hasnabad | 132 | 07:00 | 125 | 11:00 | ShahCement | 128 | 07:00 | 123 | 11:00
Hathazari | 134 | 08:00 | 130 | 16:00 | Shahjadpur | 138 | 04:00 | 131 | 18:00
Ishurdi | 139 | 09:00 | 134 | 14:00 | Shahjibazar | 132 | 07:00 | 124 | 18:00
Jaldhaka | 130 | 09:00 | 120 | 13:00 | Shahmirpur | 133 | 21:00 | 128 | 16:00
Jamalpur | 128 | 08:00 | 114 | 18:30 | Shariatpur | 134 | 08:00 | 126 | 18:00
Jashore | 135 | 09:00 | 120 | 18:30 | Sherpur | 125 | 06:00 | 114 | 13:00
Jhenaidah | 138 | 07:00 | 124 | 18:00 | Shikalbaha | 123 | 19:30 | 118 | 15:00
Jhenaidah-230 | 139 | 09:00 | 126 | 18:30 | Shikalbaha-230 | 134 | 19:00 | 130 | 00:00
Joydebpur | 140 | 00:00 | 126 | 16:00 | Shitalakhya | 131 | 07:00 | 123 | 12:00
Joypurhat | 128 | 09:00 | 122 | 14:00 | Sholosohor | 134 | 20:00 | 130 | 03:00
Juldah | 133 | 21:00 | 128 | 15:00 | Shyampur | 134 | 08:00 | 127 | 16:00
Kabirpur | 133 | 07:00 | 122 | 16:00 | Shyampur-230 | 135 | 07:00 | 128 | 16:00
Kachua | 135 | 07:00 | 127 | 04:00 | Siddhirganj | 127 | 07:00 | 123 | 12:00
Kaliakoir | 133 | 05:00 | 124 | 16:00 | Sirajganj | 132 | 09:00 | 126 | 16:00
Kallyanpur | 134 | 06:00 | 127 | 12:00 | Sonargaon | 126 | 07:00 | 120 | 16:00
Kalurghat | 134 | 19:00 | 131 | 00:00 | Sreemongol | 132 | 12:00 | 124 | 18:00
Kamrangirchar | 132 | 07:00 | 124 | 12:00 | Sreepur | 129 | 07:00 | 121 | 15:00
Kaptai | N/A | N/A | N/A | N/A | Srinagar | 131 | 06:00 | 124 | 14:00
Kasba | 126 | 07:00 | 120 | 18:00 | SSM | 134 | 00:00 | 130 | 11:00
Kazla | 132 | 08:00 | 124 | 13:00 | Sunamganj | 125 | 07:00 | 119 | 18:00
Keranigonj | 132 | 07:00 | 125 | 16:00 | Sylhet | 130 | 08:00 | 125 | 18:00
Khagrachori | 132 | 07:00 | 130 | 00:00 | Sylhet-132 | 129 | 03:00 | 126 | 18:00
Khulna | 132 | 06:00 | 121 | 18:00 | Tangail | 126 | 01:00 | 119 | 18:30
Khulna(S) | 134 | 06:00 | 125 | 18:30 | Taraganj | 132 | 09:00 | 120 | 16:00
Khulshi | 130 | 19:00 | 126 | 15:00 | Thakurgaon | 137 | 09:00 | 123 | 08:00
Kishoreganj | 127 | 07:00 | 116 | 18:00 | TK | 134 | 21:00 | 131 | 00:00
Kodda | 136 | 07:00 | 122 | 15:00 | Tongi | 136 | 00:00 | 127 | 18:00
KSRM | 133 | 06:00 | 129 | 10:00 | Ullahpara | 134 | 09:00 | 127 | 15:00
Kulaura | 134 | 07:00 | 129 | 18:30 | Ullon | 138 | 07:00 | 125 | 16:00
Kurigram | 130 | 21:00 | 119 | 13:00 | Uttara | 132 | 06:00 | 126 | 12:00
Kushtia | 135 | 06:00 | 128 | 18:00 | UttaraNew | 134 | 01:00 | 125 | 16:00
Laksam | 134 | 09:00 | 126 | 04:00 | Zigatola | 131 | 06:00 | 125 | 12:00
Lakshmipur | 130 | 07:00 | 124 | 04:00
Lalbag | 132 | 07:00 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division